Borssele Alpha and Beta Platforms

Offshore Grid NL

Employer's Requirements

General Requirements Shared Services/MIVSP

| Document number | ONL-TTB-03871 |
| --- | --- |
| Revision | 1 |
| Document status | DRAFT |

Table of Content

1	Introduction	3

1.1	Background "Wind op Zee"	3

1.2	Purpose and concept of the 700MW AC Offshore Substations	4

1.3	Background Shared Service/MIVSP	5

2	General requirements MIVSP/Shared Service systems	6

2.1	International and Dutch Laws and regulations.	6

2.2	Codes and standards	6

2.3	General Requirements	6

2.4	Earthing and bonding	6

2.4.1	Instrumentation earth	6

2.5	Lightning protection	7

2.6	Cable	7

3	Advised additional requirements to include.	7

3.1	General	7

3.2	Environmental conditions	8

3.3	Electrical Installation	8

3.4	Paint	8

# Introduction

This document describes general requirements for the sensing and communication systems which will be installed on the standardized 700MW AC Substation (platform) of TenneT and which will be procured by Rijkswaterstaat Centrale Informatievoorziening (RWS-CIV).

## Background "Wind op Zee"

The Dutch government has decided to develop 3.5 GW of wind energy production capacity offshore The Netherlands by 2023.

To achieve this the Dutch government will from 2015 onwards tender five 700 MW wind farm zones, one every consecutive year. Every wind farm zone comprises two wind farm sites of approximately 350 MW each.

Further background information concerning this development can be found in on www.windopzee.nl.

TenneT, as the offshore grid operator in the Dutch part of the North Sea, will be responsible for the design, fabrication, installation and operation of the grid connections which will transport the generated electricity to shore.

Within each of these grid connections a 700 MW AC offshore substation is included. In order to minimize the total cost of ownership, TenneT has, in-house, developed a standard platform up to the level of basic design. This basic design has been appraised by DNV GL.

The substations will be located along the Dutch coast as indicated in Figure 1-1.

Figure 1-1: Wind farm zones to be tendered are marked light blue, realised wind

farms in dark blue, future wind farm zones in yellow.

## Purpose and concept of the 700MW AC Offshore Substations

The 700 MW AC offshore substations are to carry high-voltage switching and transformation equipment as well as auxiliary facilities in support of this high-voltage equipment. Connecting power of the wind farms will be delivered to the substations at a voltage level of 66 kV, the export cables will be operated at 220 kV.

The substations are part of the larger project of grid connection realization. The other parts, being the sea cables and the onshore substation extension, will be executed in parallel to this platform contract.

Figure 1-2: The Grid Connection System (GCS)

The platforms will consist of a lift installed topside, on top of a steel jacket piled to the seabed.

Figure 1-3: Platform view.

## Background Shared Service/MIVSP

The offshore substation provides good opportunities to place meteorological, hydrological and nautical sensors and communication systems. TenneT, the wind park owners and (semi-governmental) third parties are interested in the sensing data and require these systems for their operations.

To prevent duplicate systems it has been decided that TenneT and the IT-department of the Dutch Ministry of Transport (RWS-CIV) will provide a reliable and  performant data service which will connect a variety of meteorological, hydrological and nautical sensors that can be accessed by any authorized party. RWS-CIV will install sensors on the platforms of TenneT which will be connected to the systems of the users on the shore using the fiber optic cables that will be incorporated in TenneT’s export cables .

The goal of this service is to lower the total cost of ownership of this collection of sensors for all parties by sharing infrastructure thus contributing to a reduction of the operational costs of the windfarm and to the safety on the platforms by controlling and reducing the number of maintenance activities. This implies that windfarm owners (or other parties) will have the opportunity to gain access to information of their needs by means of a data service instead of having the trouble of installing and maintaining their own set of sensors.

Subscription to the shared service will be carried out by means of service contracts that can be tailored to the exact needs of parties, describing the type of information and the required service levels. RWS-CIV will take care of all maintenance activities that will assure a reliable service.

RWS-CIV is one of the largest Dutch governmental IT organizations who have a long track record on the installation, operation and maintenance of nautical systems. Developing the Shared Service on the windfarms near the Dutch coast is fully compliant with the ambition of RWS to strengthen their position of prime IT service provider  for Dutch governmental organization and their affiliates.

# General requirements MIVSP/Shared Service systems

The various sensing and communication systems will be placed on the platforms of TenneT and therefore shall comply to the following general requirements:

## International and Dutch Laws and regulations.

The systems shall be compliant with the International and Dutch laws.

Special attention shall be given to:

- IMO (International Maritime Organization)

- Dutch electricity Act (Elektriciteitswet 1998)

- NEN 1010, Safety requirements for low-voltage installations, Oct 2015

- Mijnbouwwet, Mijnbouwbesluit, Mijnbouwregeling (Dutch Mining Regulation)

## Codes and standards

The following Codes and Standards shall be followed:

- DNVGL-ST-145 Offshore Substations (governing)

- DNVGL-OS-D201 Electrical installations

- EN 61000, (EMC) Electromagnetic compatibility (EMC)

- EN 62305, Lightning Protection systems

- ISO 9001, Quality system

## General Requirements

- The systems shall be low maintenance (max 10 hours/year).

- The systems shall be have a minimal planned maintenance interval of 0,5 year.

- The systems shall be easily maintainable.

- The systems shall be easily handled. A mechanical handling plan shall be provided (including lifting points etc.).

## Earthing and bonding

All metallic equipment shall have minimum two diagonally placed earth connection for grounding to the topside module main structure. In case the equipment is divided in several modules, each module shall have its own individual earth boss and conductor.

Earth bars, bare copper earthing cables, cable clamps, etc. exposed to marine environment shall be protected against corrosion. Lightning protection and earthing system components including fixtures, connectors, bolts, nuts, etc. shall be of marine environment quality and selected with proper consideration of foreseeable mechanical abuse.

### Instrumentation earth

Separate earthing configuration shall be provided for instrument and telecom systems. Installation method shall be chosen with regard to the functional requirements of the circuits according to the manufacturer’s instructions. Spare conductors in instrument and telecom cables shall be isolated at the field end and connected to IE earth at the source end. Distance between the PE and IE reference point shall be 1000 mm.

## Lightning protection

The lightning protection of the platform shall be carried out in accordance with instructions in EN/IEC 62305. The dimensioning of the lightning protection shall be according to protection class 1.

The lightning protection is divided into the following zones:

- Zone 0A: The external zone is the exterior of the platform. In the external zone equipment shall be protected against direct lightning stroke.

- Zone 0B: Zone where objects are not subject to direct lightning stroke, but the un- attended electromagnetic field occurs.

- Zone 1: The internal zone is the interior of the platform.

- Zone 2: The internal zone with installations located within a room.

The lightning parameters in zone 0A are selected for the protection level 1 according to table 3, EN/IEC 62305-1, and the current peak value is 200kA.

The lightning current parameters for other zones are selected as follows:

- Zone 0B: 20kA

- Zone 1: 10kA

- Zone 2: 6kA or protection not necessary.

All systems shall be designed for their specific lightning current. Futhermore special attention shall be given to prevention of lightning surges transferring from one zone to another (e.g. the application of surge arrestors on cabling when cables transfers from the outside to the inside of the platform.

## Cable

All cables shall be according DNVGL-OS-D201 Electrical installations

All cables shall be fire resistant.

# Advised additional requirements to include.

Besides the above mentioned requirement TenneT advices to incorporate the following requirements for sensing and communication systems.

## General

- The systems shall have a design life of 20 years. In these periods the systems and surfaces shall be designed to be able to withstand, with normal maintenance applied, normal wear and tear, aging and corrosion due to intended use without any need for unplanned maintenance or replacement.

- The combined systems shall have a reliability equivalent to maximum  0,25 faults per year.

- The systems and materials shall be designed for offshore environment.

- Supplier shall have offshore experience and service personnel which could perform offshore maintenance.

## Environmental conditions

The systems shall be able to withstand the following environmental conditions:

External equipment:

| Temperature | -10 − +30 degrees |
| --- | --- |
| Humidity | 0-100% |
| Offshore environment |  |

Internal equipment

| Temperature | 5 − 35 degrees |
| --- | --- |
| Humidity | 10-60% |

## Electrical Installation

- All external systems shall have an IP rating of IP56 or higher.

- All internal systems shall have an IP rating of IP22 or higher.

## Paint

Paint shall comply to one of the following codes/standards or comparable

- NORSOK M-501, Surface preparation and protective coating

- ISO 12955,  (Class C5M, durability >15 year)