## Scope 2022
nr | Activity | Comment | Carried out by | Ordered / optional
in advance
1 | new first stage compressorblades | purchase | Contractor
2 | new exhaust frame | purchase | Contractor
3 | new diffusor | purchase | Contractor
4 | new shrouded S17s, EGV1s and EGV2s and modified inner barrel | Purchase according TIL2092 | Contractor
Preliminary
5 | Finalize Quality Plan / safety plan | incl. PSSB20180709A-R1 | Contractor / UBX
6 | Mobilization |  | Contractor
7 | Inspect parts and spares needed | list checked by UBX on availabilty in store | Contractor
8 | Built scaffolding | preferred supplier | UBX
9 | Safe guarding installation |  | UBX
10 | Condition monitoring UBS |  | UBX
11 | 6-point measurement compressor before disassembly |  | Contractor
12 | Inspection availablity neccesary hoisting parts
13 | availabilty special tooling (bolt tensing, spark eroding etc)
Disassembly
14 | Insulation | preferred supplier | Contractor
15 | Lights, fans and fire alarms GT housing |  | Contractor / UBX
16 | Enclosure inletduct and gassystem |  | Contractor
17 | gas heater | cleaning air side | Contractor
18 | Compensator inletduct | replace | Contracor
19 | Air inlet filters | depend on inspection | UBX | Contractor
20 | Exhaustduct casing and diffusor | repair casing and renew diffusor | Contractor
21 | Seal exhaust diffusor | replace | Contractor
22 | Assemble ratchet |  | Contractor
23 | Gears IGV's to restore backlash | renew rack | Contractor
24 | Cool lines and other lines where needed |  | Contractor
25 | Fuel lines | replace all flexables | Contractor
26 | Primairy fuel nozzles | replace | Contractor
27 | Secundary fuel nozzles | replace | Contractor
28 | Spark plugs and flame detectors | replace 2 sparkplugs/ flame det | Contractor
29 | Combustion chambers |  | Contractor
30 | Cross fire tubes /retainers | replace | Contractor
31 | Liners | replace | Contractor
32 | Flow sleeves |  | Contractor
33 | Fix supports GT casing |  | Contractor
34 | Remove bolts turbine casing |  | Contractor
35 | Wrapper house |  | Contractor
36 | Turbine casing |  | Contractor
37 | exhaust frame | renew | Contractor
38 | Transition pieces / side seals | replace side seals 14 pieces | Contractor | order side seals
39 | Bull hornes | replace | Contractor
40 | forward compressor casing |  | Contractor
41 | compressor casing |  | Contractor
42 | compressor discharge |  | Contractor
43 | removal S17s,EGV1s and EGV2s | renew for shrouded ones
44 | compressor discharge casing repair grooves |  | Contractor
45 | removal upper part bearing 1,2 and 3 |  | Contractor
46 | disconnect couplings and remove shaft to generator | renew coupling bolts GT side | Contractor
47 | remove rotor | including transport, storage, cleaning compressor part | Contractor
48 | remove 1st stage compressor blades | renew 1st stage compressor blades | Contractor
49 | 1st stage nozzle (upper- and lower half) | replace | Contractor
50 | 1st stage nozzle (excenterpens and clamps) | replace | Contractor
51 | 1st stage buckets | replace | Contractor
52 | 1st stage shrouds (upper and lower) | replace | Contractor
53 | 2nd stage buckets >72000 | replace | Contractor
54 | 2nd stage nozzles >72000 | replace | Contractor
55 | 2nd stage shrouds >72000 | replace | Contractor
56 | 3rd stage buckets >96000 | replace | Contractor
57 | 3rd stage nozzles >96000 | replace | Contractor
58 | 3rd stage shrouds >96000 | replace | Contractor
59 | Innerbarrel (incl. brush seals) | new modified inner barrel | Contractor
60 | Rotor seal stator 2nd stage turbine (discourager seal) | replace | Contractor
61 | bearing housing 1 |  | Contractor
62 | bearing housing 2 | replace brush seal (TIL 1643) | Contractor
63 | bearing housing 3 |  | Contractor
Inspections, measurements & repairs
64 | All preparations for Non Destructive Examination |  | Contractor
65 | Check rotor position | before removal rotor | Contractor
66 | check alignment main coupling | before removal rotor | Contractor
67 | Axial measurement GT | before removal rotor | Contractor
68 | Measurement turbine clearences | before removal rotor | Contractor
69 | Inspect IGV's (bushing wear, backlash) | including angle measurement | Contractor
70 | Inspect flowsleeves | refurbish during outage | Contractor
71 | Check and clean fuel nozzles |  | Contractor
72 | fuel nozzles flowtest and match gasplates |  | UBX
73 | Spark plugs and flame detectors |  | Contractor
74 | Wiring wheelspacecouples |  | Contractor
75 | 1st, 2nd and 3rd stage nozzles |  | Contractor
76 | 1st, 2nd and 3rd stage buckets |  | Contractor
77 | 1st, 2nd and 3rd stage shrouds |  | Contractor
78 | rotor inspection | TIL1576-R1, TIL1049-R3, TIL1975-R1, TIL2054, TIL2056 | Contractor
79 | compressor discharge casing repair grooves |  | Contractor
80 | Check alternative repair grooves S17, EGV1 and EGV2 | repair when necessary and NDO | Contractor
81 | renew 1st stage compressor blades |  | Contractor
82 | Inspect, measure and correct compressor blades |  | Contractor
83 | inspect bearing 1 |  | Contractor
84 | inspect bearing 2 |  | Contractor
85 | inspect bearing 3 |  | Contractor
86 | renew diffusor |  | Contractor
87 | inspect auxiliary gearbox and main oil pump | replace coupling and check alignment | Contractor
88 | renew exhaust casing | according proposal | Contractor
89 | Dovetails turbinewheels |  | Contractor
90 | Repair thead holes casing | EDH, helicoils | Contractor
91 | bell mouth | renew coating
92 | Foundation |  | Contractor
93 | Bleedvalves | open, inspect, repair and test | Contractor
94 | Gasvalves and controls | inspect and overhaul | Contractor
95 | Check allignment accessory coupling | if necessary | Contractor
96 | Lube- and control oil filters | replace / 24 pieces | UBX | Contractor
97 | accumulator oil system | test | Contractor
98 | Lube- and control oil coolers | clean and check | Contractor
99 | Implosion hatches | calibrate | Contractor
100 | Check and grease sliding surfaces |  | Contractor
101 | Nozzles and lines washunit | inspect and clean | Contractor
102 | Check main- and auxiliary gearbox |  | Contractor
103 | Exhaustduct casing and diffusor connection | repair casing renew diff. connection | Contractor
104 | Air inletfilter housing | inspect and clean | Contractor
105 | Check elbow flowplates | check for cracks | Contractor
106 | Check flexible gashoses and -lines | renew all hoses | Contractor
107 | Technical cleaning parts |  | Contractor
108 | Commisioning |  | Contractor
Assembly
109 | bearing housing 1 |  | Contractor
110 | bearing housing 2 |  | Contractor
111 | bearing housing 3 |  | Contractor
112 | 1st stage nozzles (upper- and lower half) | incl. excenterpens and clamps | Contractor
113 | 1st stage buckets |  | Contractor
114 | 1st stage shrouds (upper and lower) |  | Contractor
115 | 2nd stage buckets | if necessary | Contractor
116 | 3rd stage buckets | if necessary | Contractor
117 | Check turbine clearences |  | Contractor
118 | Bullhorns |  | Contractor
119 | Transition pieces |  | Contractor
120 | Turbine casing |  | Contractor
121 | Wrapperhouse |  | Contractor
122 | bearing 2 drain flange | TIL1910-R1 | Contractor
123 | Support gasturbine |  | Contractor
124 | Combustion chambers + covers |  | Contractor
125 | Cross fire tubes (inner and outer pipes) |  | Contractor
126 | Flow sleeves |  | Contractor
127 | Liners |  | Contractor
128 | Spark plugs and flame detectors |  | Contractor
129 | Primaire and secundaire fuelnozzles |  | Contractor
130 | Cool lines and other lines needed |  | Contractor
131 | Fuel lines and hoses |  | Contractor
132 | 6 point measurement compressor (after assembly) |  | Contractor
133 | Casing and fans |  | Contractor/UBX
134 | Insulation |  | Contractor
135 | Turbine cover and lights |  | Contractor / UBX
136 | Tape gasflanges |  | Contractor
137 | Connect electrical systems |  | Contractor
138 | Connect fire alarms |  | Contractor / UBX
139 | Clean workspace |  | Contractor
140 | DLN tuning |  | Contractor
141 | commisioning |  | Contractor
142 | Project rapport |  | Contractor
extra work
143 | repair exhaust duct |  | UBX
144 | fans turbine housing and exhaust frame clean and inspect | electrical motor replace bearings | Contractor
145 | replace lube oil gasturbine |  | UBX
146 | inspection of axillary and emergency oil pump |  | Contractor
147 | cleaning gas heater on roof enclosure |  | Contractor
Instrumentation inspections
148 | Testing fire protection installation (high safe) |  | Contractor
149 | Inspection wiring Enclosure and vans |  | Contractor
150 | Testing flame detection and ignitors |  | Contractor
151 | Testing bleedvalves |  | Contractor
152 | Wheelspacekoppels |  | Contractor
153 | Exhaustthermokoppels incl junction boxes |  | Contractor
154 | Compressor thermocouples and transmitters |  | Contractor
155 | Insp. and calibrate IGV-systeem |  | Contractor
156 | Insp. and calibrate gasvalves GCV,GSRV,GSV en GTV |  | Contractor
157 | Insp. and adjust transmitters, pressostaten and thermostaten |  | Contractor
158 | Insp. And testing Solenoïde valves |  | Contractor
159 | Inspect hydraulic system and accumulators |  | Contractor
160 | Insp. false start drain valves |  | Contractor
161 | Insp and controle Speedtronic Mk5 |  | Contractor