## Slide 1: VNX Profile - VEN-VNX01
Project:
09/21/2020, 01:21 (UTC +02:00)
Everon Maria, everon.maria@dell.com
Pascal Bemelmans, pascal.bemelmans@l1.nl
1139411
VEN-VNX01
Project ID:
Prepared For:
Prepared By:
Created:
PPTX 2018.08.14
Copyright © 2020 Dell Inc.

## Slide 2: Common Summary: Inventory, Capacity and Workload
Serial No. | CKM00133601309
Model No. | VNX_5400
Software Level | 5.33.184
System Cache (GB) | 32
Fast Cache Enabled | False
Fast Cache (GB) | 0
Total No. Drives | 97
No. SSD Drives | 0
No. HDD Drives | 97
Usable SSD Capacity (TB) | 0.0
Usable HDD Capacity (TB) | 251.16
Subscription % | 94.04%
Subscription Capacity (TB) | 192
Used Capacity TB | 175.29
Configured Capacity (TB) | 204.21
LUN Skew - Avg IO | 76.2%
Configuration File Date | 2020-09-14
Performance Start | 2020-09-14 10:24:45
Performance End | 2020-09-21 00:58:15
Performance Interval | 1 mins
Peak IOPS: Date Time | 2020-09-15 02:32:11
Peak IOPS: IOPS | 11641
Peak IOPS: Read % | 33
Peak IOPS: Avg. Read Size (KB) | 7.99
Peak IOPS: Avg. Write Size (KB) | 8.13
Peak IOPS: MB/s | 91.92
Peak IOPS: Latency (ms) | 1.4
95th IOPS: Date Time | 2020-09-16 09:09:46
95th IOPS: IOPS | 5,069
95th IOPS: Read % | 0
95th IOPS: Avg. Read Size (KB) | 4.77
Inventory and Capacity Summary
Workload Summary Peak IOP Measurements
Workload Summary 95th Percentile Measurements
Workload Summary Peak MB/s Measurements
Peak MB/s: Date Time | 2020-09-16 02:17:13
Peak MB/s: IOPS | 11587
Peak MB/s: Read % | 21
Peak MB/s: Avg. Read Size (KB) | 7.97
Peak MB/s: Avg. Write Size (KB) | 8.73
Peak MB/s: MB/s | 96.97
Peak MB/s: Latency (ms) | 1.4
Copyright © 2020 Dell Inc.
PPTX 2018.08.14

## Slide 3: Summary - VEN-VNX01
Snap View | Yes
Mirror View | Yes
Recover Point | Yes
SAN Copy | Yes
Configuration File Date | 2020-09-14
Performance Start | 2020-09-14 10:24
Performance End | 2020-09-21 00:58
Performance Interval (mins) | 1 mins
FC 4GB | 0
FC 8GB | 4
FC 16GB | 0
1 GigE | 8
10 GigE | 0
iSCSI | 8
File | Yes
Block | No
Serial No. | CKM00133601309
Model No. | VNX_5400
Software Level | 5.33.184
System Cache (GB) | 32
No. DAEs | 8
Active Drives | 88
Inactive Drives | 9
Empty Slots | 33
Hardware Overview
Software Features
Input Data
Connectivity
Emulations
Copyright © 2020 Dell Inc.
PPTX 2018.08.14

## Slide 4: Capacity Summary by Drive Type - VEN-VNX01
Name | Model | Total Raw Capacity (TB) | Usable SSD (TB) | Configured Capacity (TB) | Used (TB) | Utilization (%)
VEN-VNX01 | VNX_5400 | 251.16 | 0.0 | 204.21 | 175.29 | 86
Drive Type | Rotational Speed (K) | Number of Spare Drive | Number of Data Drive | Raw Size (GB) | Number of Drives | Raw Capacity (TB) | Raw Capacity (%)
Empty Slot | Empty | 0 | 0 | 0 | 33 | 0.0 | 0.0
HDD | 7.2 | 3 | 88 | 2,751 | 91 | 244.47 | 97.34
HDD | Unknown | 1 | 0 | 2,751 | 1 | 2.69 | 1.07
HDD | 10 | 5 | 0 | 820 | 5 | 4.0 | 1.59
Copyright © 2020 Dell Inc.
PPTX 2018.08.14
Notes: Utilization (%) is calculated by dividing Used(TB) by Usable (TB). Used/Usable * 100 = Utilization %

## Slide 5: Array Profile Metric - VEN-VNX01
Number of Disks | 97
Usable HDD (TB) | 251.16
Usable SSD (TB) | 0.0
Raw Capacity (TB) | 251.16
Used Capacity(TB) | 175.29
LUN Skew | 76% of IOPS/24% of LUNS
Front End MB/sec - max | 97
Date Time- Peak | 2020-09-15 02:32:11
IOPS at Peak | 11,641
Read % at Peak | 33.00
Read Size (KB) at Peak | 7.99
Write Size (KB) at Peak | 8.13
MB/sec at Peak | 92
Latency (ms) at Peak | 1.4
Copyright © 2020 Dell Inc.
PPTX 2018.08.14
Notes: SSD is the total RAW physical capacity of the array. LUN is the summation of the total volume size. LUN used is the amount of non-zero data written to the array before compression and deduplication. The rest measures a peak. This slide is designed to show in one slide all of the KPIs for sizing.

## Slide 6: 5 Year Growth Projection - VEN-VNX01
Copyright © 2020 Dell Inc.
At 20% growth, usable capacity will be exceeded in less than 1 year.
PPTX 2018.08.14

## Slide 7: Array Profile Details

## Slide 8: Array Capacity - VEN-VNX01
Copyright © 2020 Dell Inc.
PPTX 2018.08.14

## Slide 9: Fibre Channel Ports - VEN-VNX01
Name | Speed (Gbit/sec) | Read MB/sec 95th | Write MB/sec 95th
Port 0 [FC; 50:06:01:60:88:60:14:4D:50:06:01:60:08:60:14:4D ] | 0 | 0 | 0
Port 0 [FC; 50:06:01:60:88:60:14:4D:50:06:01:68:08:60:14:4D ] | 0 | 0 | 0
Port 1 [FC; 50:06:01:60:88:60:14:4D:50:06:01:61:08:60:14:4D ] | 0 | 0 | 0
Port 1 [FC; 50:06:01:60:88:60:14:4D:50:06:01:69:08:60:14:4D ] | 0 | 0 | 0
Port 10 [iSCSI; iqn.1992-04.com.emc:cx.ckm00133601309.a10 ] | 1 | 0 | 0
Port 10 [iSCSI; iqn.1992-04.com.emc:cx.ckm00133601309.b10 ] | 1 | 0 | 0
Port 11 [iSCSI; iqn.1992-04.com.emc:cx.ckm00133601309.a11 ] | 1 | 0 | 0
Port 11 [iSCSI; iqn.1992-04.com.emc:cx.ckm00133601309.b11 ] | 1 | 0 | 0
Port 2 [FC; 50:06:01:60:88:60:14:4D:50:06:01:62:08:60:14:4D ] | 0 | 0 | 0
Port 2 [FC; 50:06:01:60:88:60:14:4D:50:06:01:6A:08:60:14:4D ] | 0 | 0 | 0
Port 3 [FC; 50:06:01:60:88:60:14:4D:50:06:01:63:08:60:14:4D ] | 0 | 0 | 0
Port 3 [FC; 50:06:01:60:88:60:14:4D:50:06:01:6B:08:60:14:4D ] | 0 | 0 | 0
Copyright © 2020 Dell Inc.
PPTX 2018.08.14

## Slide 10: Fibre Channel Ports - VEN-VNX01
Name | Speed (Gbit/sec) | Read MB/sec 95th | Write MB/sec 95th
Port 4 [FC; 50:06:01:60:88:60:14:4D:50:06:01:64:08:60:14:4D ] | 8 | 0 | 5
Port 4 [FC; 50:06:01:60:88:60:14:4D:50:06:01:6C:08:60:14:4D ] | 8 | 0 | 5
Port 5 [FC; 50:06:01:60:88:60:14:4D:50:06:01:65:08:60:14:4D ] | 8 | 0 | 0
Port 5 [FC; 50:06:01:60:88:60:14:4D:50:06:01:6D:08:60:14:4D ] | 8 | 0 | 0
Port 6 [FC; 50:06:01:60:88:60:14:4D:50:06:01:66:08:60:14:4D ] | 0 | 0 | 0
Port 6 [FC; 50:06:01:60:88:60:14:4D:50:06:01:6E:08:60:14:4D ] | 0 | 0 | 0
Port 7 [FC; 50:06:01:60:88:60:14:4D:50:06:01:67:08:60:14:4D ] | 0 | 0 | 0
Port 7 [FC; 50:06:01:60:88:60:14:4D:50:06:01:6F:08:60:14:4D ] | 0 | 0 | 0
Port 8 [iSCSI; iqn.1992-04.com.emc:cx.ckm00133601309.a8 ] | 1 | 0 | 0
Port 8 [iSCSI; iqn.1992-04.com.emc:cx.ckm00133601309.b8 ] | 1 | 0 | 0
Port 9 [iSCSI; iqn.1992-04.com.emc:cx.ckm00133601309.a9 ] | 1 | 0 | 0
Port 9 [iSCSI; iqn.1992-04.com.emc:cx.ckm00133601309.b9 ] | 1 | 0 | 0
Copyright © 2020 Dell Inc.
PPTX 2018.08.14

## Slide 11: Performance Profile - VEN-VNX01
Copyright © 2020 Dell Inc.
PPTX 2018.08.14

## Slide 12: Front End Ports: Peak Composite
Copyright © 2019 Dell Inc.
Chart: 
Chart: 

## Slide 13: Cache Utilization
SP-B
Chart: Cache Flush (MB/s)
Chart: Cache Flush (MB/s)
Copyright © 2019 Dell Inc.
SP-A

## Slide 14: Peak/Average Ports Utilization
Chart: 
| SPA 4 | SPA 5 | SPA 8 | SPA 9 | SPA 10 | SPA 11
Peak 0-25% | 8 | 0 | 0 | 0 | 0 | 0
Peak 26-69%
Peak 70-89%
Peak 90-100%
Average 0-25% | 0 | 0 | 0 | 0 | 0 | 0
Average 26-69%
Average 70-89%
Average 90-100%
Baseline | 0 | 0 | 0 | 0 | 0 | 0
Peak Timestamp
Chart: 
| SPB 4 | SPB 5 | SPB 8 | SPB 9 | SPB 10 | SPB 11
Peak 0-25% | 7 | 0 | 0 | 0 | 0 | 0
Peak 26-69%
Peak 70-89%
Peak 90-100%
Average 0-25% | 0 | 0 | 0 | 0 | 0 | 0
Average 26-69%
Average 70-89%
Average 90-100%
Baseline | 0 | 0 | 0 | 0 | 0 | 0
Peak Timestamp
Copyright © 2019 Dell Inc.
Peak Utilization
Average Utilization
Notes: FE Port Utilization – Avg/Peak

## Slide 15: Storage Processor Utilization
Copyright © 2020 Dell Inc.
PPTX 2018.08.14

## Slide 16: Front End Latency - VEN-VNX01
Copyright © 2020 Dell Inc.
PPTX 2018.08.14

## Slide 17: Front End Bandwidth - VEN-VNX01
Copyright © 2020 Dell Inc.
PPTX 2018.08.14

## Slide 18: Front End IOPS vs Back End IOPS - VEN-VNX01
Copyright © 2020 Dell Inc.
PPTX 2018.08.14

## Slide 19: Top 1 Clients by IOPS - VEN-VNX01
Copyright © 2020 Dell Inc.
PPTX 2018.08.14

## Slide 20: Top 1 Clients by IOPS - VEN-VNX01
Client | #LUNs | Used (TB) | Peak IOPS | Response Time (ms) | Front End MB/sec | Read % | Avg IO Size (KB)
Celerra_VEN-CS0-VNX01 | 30 | 7.28 | 11,641 | 1.21 | 6 | 8.31% | 9.04
PPTX 2018.08.14
Copyright © 2020 Dell Inc.

## Slide 21: IO Size and Read Percent - VEN-VNX01
Copyright © 2020 Dell Inc.
PPTX 2018.08.14

## Slide 22: IOPS Thresholds - VEN-VNX01
Copyright © 2020 Dell Inc.
PPTX 2018.08.14

## Slide 23: Back End Activity By Pool - VEN-VNX01
Copyright © 2020 Dell Inc.
PPTX 2018.08.14

## Slide 24: Back End Activity By Pool - VEN-VNX01
Copyright © 2020 Dell Inc.
PPTX 2018.08.14

## Slide 25: Back End Activity By Pool - VEN-VNX01
Copyright © 2020 Dell Inc.
PPTX 2018.08.14

## Slide 26: Total Queue Length - VEN-VNX01
Copyright © 2020 Dell Inc.
PPTX 2018.08.14

## Slide 27: Top Clients and LUNs

## Slide 28: Top 15 LUNs by IOPS - VEN-VNX01
LUN | Front End IOPS - max | Front End MB/sec-max | Avg IO Size (KB) | Latency (ms) - max | Latency (ms) - avg | Read % - avg
LUN-File-NLSAS_18 | 4,079 | 38 | 9.94 | 6.20 | 1.10 | 0.79%
LUN-File-NLSAS_19 | 2,995 | 28 | 9.42 | 1.30 | 0.71 | 0.52%
LUN-File-NLSAS_17 | 2,789 | 23 | 8.17 | 8.50 | 0.98 | 1.83%
LUN-File-NLSAS_16 | 2,780 | 23 | 8.54 | 8.70 | 0.94 | 1.91%
LUN-File-NLSAS_15 | 2,369 | 23 | 9.45 | 8.00 | 0.88 | 1.82%
LUN-File-NLSAS_0 | 2,342 | 19 | 8.39 | 10.60 | 1.67 | 22.6%
LUN-File-NLSAS_1 | 2,328 | 18 | 8.31 | 10.30 | 1.65 | 22.71%
LUN-File-NLSAS_3 | 2,328 | 18 | 8.81 | 10.40 | 1.64 | 22%
LUN-File-NLSAS_2 | 2,325 | 18 | 8.68 | 10.30 | 1.63 | 21.97%
LUN-File-NLSAS_4 | 2,322 | 18 | 9.16 | 9.50 | 1.62 | 20.5%
PPTX 2018.08.14
Copyright © 2020 Dell Inc.
Notes: This shows the top 15 LUNS by IOPS

## Slide 29: Top 15 LUNs by IOPS - VEN-VNX01
LUN | Front End IOPS - max | Front End MB/sec-max | Avg IO Size (KB) | Latency (ms) - max | Latency (ms) - avg | Read % - avg
LUN-File-NLSAS_7 | 1,358 | 11 | 8.29 | 8.90 | 1.18 | 12.62%
LUN-File-NLSAS_6 | 1,356 | 11 | 8.07 | 11.40 | 1.22 | 12.8%
LUN-File-NLSAS_5 | 1,350 | 11 | 8.22 | 4.20 | 1.21 | 12.76%
LUN-File-NLSAS_9 | 1,349 | 11 | 8.57 | 6.30 | 1.18 | 12.34%
LUN-File-NLSAS_8 | 1,347 | 11 | 8.07 | 5.20 | 1.23 | 12.83%
PPTX 2018.08.14
Copyright © 2020 Dell Inc.
Notes: This shows the top 15 LUNS by IOPS

## Slide 30: Top 15 LUNs by MBPS - VEN-VNX01
LUN | Front End IOPS - max | Front End MB/sec-max | Avg IO Size (KB) | Latency (ms) - max | Latency (ms) - avg | Read % - avg
LUN-File-NLSAS_18 | 4,079 | 38 | 9.94 | 6.20 | 1.10 | 0.79%
LUN-File-NLSAS_19 | 2,995 | 28 | 9.42 | 1.30 | 0.71 | 0.52%
LUN-File-NLSAS_15 | 2,369 | 23 | 9.45 | 8.00 | 0.88 | 1.82%
LUN-File-NLSAS_17 | 2,789 | 23 | 8.17 | 8.50 | 0.98 | 1.83%
LUN-File-NLSAS_16 | 2,780 | 23 | 8.54 | 8.70 | 0.94 | 1.91%
LUN-File-NLSAS_0 | 2,342 | 19 | 8.39 | 10.60 | 1.67 | 22.6%
LUN-File-NLSAS_1 | 2,328 | 18 | 8.31 | 10.30 | 1.65 | 22.71%
LUN-File-NLSAS_3 | 2,328 | 18 | 8.81 | 10.40 | 1.64 | 22%
LUN-File-NLSAS_2 | 2,325 | 18 | 8.68 | 10.30 | 1.63 | 21.97%
LUN-File-NLSAS_4 | 2,322 | 18 | 9.16 | 9.50 | 1.62 | 20.5%
PPTX 2018.08.14
Copyright © 2020 Dell Inc.
Notes: This shows the top 15 LUNS by IOPS

## Slide 31: Top 15 LUNs by MBPS - VEN-VNX01
LUN | Front End IOPS - max | Front End MB/sec-max | Avg IO Size (KB) | Latency (ms) - max | Latency (ms) - avg | Read % - avg
LUN-File-NLSAS_7 | 1,358 | 11 | 8.29 | 8.90 | 1.18 | 12.62%
LUN-File-NLSAS_6 | 1,356 | 11 | 8.07 | 11.40 | 1.22 | 12.8%
LUN-File-NLSAS_9 | 1,349 | 11 | 8.57 | 6.30 | 1.18 | 12.34%
LUN-File-NLSAS_5 | 1,350 | 11 | 8.22 | 4.20 | 1.21 | 12.76%
LUN-File-NLSAS_8 | 1,347 | 11 | 8.07 | 5.20 | 1.23 | 12.83%
PPTX 2018.08.14
Copyright © 2020 Dell Inc.
Notes: This shows the top 15 LUNS by IOPS