## Slide 1: VNX Profile - MAA-VNX01
Project:
04/28/2020, 05:06 (UTC +02:00)
Demian Geven, demian.geven@l1.nl
1044576
VNX L1
Project ID:
Prepared For:
Created:
PPTX 2018.08.14
Copyright © 2020 Dell Inc.

## Slide 2: Common Summary: Inventory, Capacity and Workload
Serial No. | CKM00133700906
Model No. | VNX_5400
Software Level | 5.33.184
System Cache (GB) | 32
Fast Cache Enabled | True
Fast Cache (GB) | 275
Total No. Drives | 155
No. SSD Drives | 7
No. HDD Drives | 148
Usable SSD Capacity (TB) | 0.62
Usable HDD Capacity (TB) | 257.0
Subscription % | 93.67%
Subscription Capacity (TB) | 192.96
Used Capacity TB | 186.1
Configured Capacity (TB) | 205.78
LUN Skew - Avg IO | 77%
Configuration File Date | 2020-04-20
Performance Start | 2020-04-20 10:52:18
Performance End | 2020-04-27 01:25:51
Performance Interval | 1 mins
Peak IOPS: Date Time | 2020-04-23 12:04:34
Peak IOPS: IOPS | 11318
Peak IOPS: Read % | 84
Peak IOPS: Avg. Read Size (KB) | 16.69
Peak IOPS: Avg. Write Size (KB) | 66.05
Peak IOPS: MB/s | 274.09
Peak IOPS: Latency (ms) | 6.6
95th IOPS: Date Time | 2020-04-25 00:40:15
95th IOPS: IOPS | 6,002
95th IOPS: Read % | 78
95th IOPS: Avg. Read Size (KB) | 33.61
Inventory and Capacity Summary
Workload Summary Peak IOP Measurements
Workload Summary 95th Percentile Measurements
Workload Summary Peak MB/s Measurements
Peak MB/s: Date Time | 2020-04-24 18:21:34
Peak MB/s: IOPS | 7472
Peak MB/s: Read % | 65
Peak MB/s: Avg. Read Size (KB) | 59.74
Peak MB/s: Avg. Write Size (KB) | 93.86
Peak MB/s: MB/s | 524.07
Peak MB/s: Latency (ms) | 18.8
Copyright © 2020 Dell Inc.
PPTX 2018.08.14

## Slide 3: Summary - MAA-VNX01
Snap View | Yes
Mirror View | Yes
Recover Point | Yes
SAN Copy | Yes
Configuration File Date | 2020-04-20
Performance Start | 2020-04-20 10:53
Performance End | 2020-04-27 01:25
Performance Interval (mins) | 1 mins
FC 4GB | 0
FC 8GB | 4
FC 16GB | 0
1 GigE | 0
10 GigE | 0
iSCSI | 4
File | Yes
Block | Yes
Serial No. | CKM00133700906
Model No. | VNX_5400
Software Level | 5.33.184
System Cache (GB) | 32
No. DAEs | 9
Active Drives | 144
Inactive Drives | 11
Empty Slots | 10
Hardware Overview
Software Features
Input Data
Connectivity
Emulations
Copyright © 2020 Dell Inc.
PPTX 2018.08.14

## Slide 4: Capacity Summary by Drive Type - MAA-VNX01
Name | Model | Total Raw Capacity (TB) | Usable SSD (TB) | Configured Capacity (TB) | Used (TB) | Utilization (%)
MAA-VNX01 | VNX_5400 | 257.63 | 0.62 | 205.78 | 186.1 | 90
Drive Type | Rotational Speed (K) | Number of Spare Drive | Number of Data Drive | Raw Size (GB) | Number of Drives | Raw Capacity (TB) | Raw Capacity (%)
Unknown | Flash | 10 | 0 | 0 | 10 | 0.0 | 0.0
HDD | 7.2 | 3 | 80 | 2,751 | 83 | 222.98 | 86.55
HDD | 10 | 7 | 58 | 536 | 65 | 34.02 | 13.21
SSD | Flash | 1 | 6 | 91 | 7 | 0.62 | 0.24
Copyright © 2020 Dell Inc.
PPTX 2018.08.14
Notes: Utilization (%) is calculated by dividing Used(TB) by Usable (TB). Used/Usable * 100 = Utilization %

## Slide 5: Array Profile Metric - MAA-VNX01
Number of Disks | 155
Usable HDD (TB) | 257
Usable SSD (TB) | 0.62
Raw Capacity (TB) | 257.63
Used Capacity(TB) | 186.1
LUN Skew | 77% of IOPS/23% of LUNS
Front End MB/sec - max | 524
Date Time- Peak | 2020-04-23 12:04:34
IOPS at Peak | 11,318
Read % at Peak | 84.00
Read Size (KB) at Peak | 16.69
Write Size (KB) at Peak | 66.05
MB/sec at Peak | 274
Latency (ms) at Peak | 6.6
Copyright © 2020 Dell Inc.
PPTX 2018.08.14
Notes: SSD is the total RAW physical capacity of the array. LUN is the summation of the total volume size. LUN used is the amount of non-zero data written to the array before compression and deduplication. The rest measures a peak. This slide is designed to show in one slide all of the KPIs for sizing.

## Slide 6: 5 Year Growth Projection - MAA-VNX01
Copyright © 2020 Dell Inc.
At 20% growth, usable capacity will be exceeded in less than 1 year.
PPTX 2018.08.14

## Slide 7: Array Profile Details

## Slide 8: Array Capacity - MAA-VNX01
Copyright © 2020 Dell Inc.
PPTX 2018.08.14

## Slide 9: Fibre Channel Ports - MAA-VNX01
Name | Speed (Gbit/sec) | Read MB/sec 95th | Write MB/sec 95th
Port 0 [FC; 50:06:01:60:88:60:14:25:50:06:01:60:08:60:14:25 ] | 0 | 0 | 0
Port 0 [FC; 50:06:01:60:88:60:14:25:50:06:01:68:08:60:14:25 ] | 0 | 0 | 0
Port 1 [FC; 50:06:01:60:88:60:14:25:50:06:01:61:08:60:14:25 ] | 0 | 0 | 0
Port 1 [FC; 50:06:01:60:88:60:14:25:50:06:01:69:08:60:14:25 ] | 0 | 0 | 0
Port 2 [FC; 50:06:01:60:88:60:14:25:50:06:01:62:08:60:14:25 ] | 0 | 0 | 0
Port 2 [FC; 50:06:01:60:88:60:14:25:50:06:01:6A:08:60:14:25 ] | 0 | 0 | 0
Port 3 [FC; 50:06:01:60:88:60:14:25:50:06:01:63:08:60:14:25 ] | 0 | 0 | 0
Port 3 [FC; 50:06:01:60:88:60:14:25:50:06:01:6B:08:60:14:25 ] | 0 | 0 | 0
Port 4 [FC; 50:06:01:60:88:60:14:25:50:06:01:64:08:60:14:25 ] | 8 | 1 | 28
Port 4 [FC; 50:06:01:60:88:60:14:25:50:06:01:6C:08:60:14:25 ] | 8 | 1 | 30
Port 5 [FC; 50:06:01:60:88:60:14:25:50:06:01:65:08:60:14:25 ] | 8 | 0 | 1
Port 5 [FC; 50:06:01:60:88:60:14:25:50:06:01:6D:08:60:14:25 ] | 8 | 0 | 0
Copyright © 2020 Dell Inc.
PPTX 2018.08.14

## Slide 10: Fibre Channel Ports - MAA-VNX01
Name | Speed (Gbit/sec) | Read MB/sec 95th | Write MB/sec 95th
Port 6 [FC; 50:06:01:60:88:60:14:25:50:06:01:66:08:60:14:25 ] | 0 | 0 | 0
Port 6 [FC; 50:06:01:60:88:60:14:25:50:06:01:6E:08:60:14:25 ] | 0 | 0 | 0
Port 7 [FC; 50:06:01:60:88:60:14:25:50:06:01:67:08:60:14:25 ] | 0 | 0 | 0
Port 7 [FC; 50:06:01:60:88:60:14:25:50:06:01:6F:08:60:14:25 ] | 0 | 0 | 0
Port 8 [iSCSI; iqn.1992-04.com.emc:cx.ckm00133700906.a8 ] | 16 | 11 | 4
Port 8 [iSCSI; iqn.1992-04.com.emc:cx.ckm00133700906.b8 ] | 16 | 14 | 5
Port 9 [iSCSI; iqn.1992-04.com.emc:cx.ckm00133700906.a9 ] | 16 | 11 | 4
Port 9 [iSCSI; iqn.1992-04.com.emc:cx.ckm00133700906.b9 ] | 16 | 14 | 5
Copyright © 2020 Dell Inc.
PPTX 2018.08.14

## Slide 11: Performance Profile - MAA-VNX01
Copyright © 2020 Dell Inc.
PPTX 2018.08.14

## Slide 12: Front End Ports: Peak Composite
Copyright © 2019 Dell Inc.
Chart: 
26-69% | 27 | 33 | 26 | 43 | 26 | 37 | 36 | 40 | 39 | 27
70-89%
90-100%
Chart: 
26-69% | 30 | 26 | 30 | 27 | 0 | 26 | 0 | 27 | 30 | 0 | 0 | 0 | 0 | 0
70-89% | 0 | 0 | 0 | 0 | 0 | 0 | 0
90-100% | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Slide 13: Cache Utilization
SP-B
Chart: Cache Flush (MB/s)
Chart: Cache Flush (MB/s)
Copyright © 2019 Dell Inc.
SP-A

## Slide 14: Peak/Average Ports Utilization
Chart: 
| SPA 4 | SPA 5 | SPA 8 | SPA 9
Peak 0-25% | 5 | 9 | 9
Peak 26-69% | 30
Peak 70-89%
Peak 90-100%
Average 0-25% | 2 | 0 | 0 | 0
Average 26-69%
Average 70-89%
Average 90-100%
Baseline | 0 | 0 | 0 | 0
Peak Timestamp
Chart: 
| SPB 4 | SPB 5 | SPB 8 | SPB 9
Peak 0-25% | 0 | 12 | 12
Peak 26-69% | 43
Peak 70-89%
Peak 90-100%
Average 0-25% | 2 | 0 | 1 | 1
Average 26-69%
Average 70-89%
Average 90-100%
Baseline | 0 | 0 | 0 | 0
Peak Timestamp
Copyright © 2019 Dell Inc.
Peak Utilization
Average Utilization
Notes: FE Port Utilization – Avg/Peak

## Slide 15: Storage Processor Utilization
Copyright © 2020 Dell Inc.
PPTX 2018.08.14

## Slide 16: Front End Latency - MAA-VNX01
Copyright © 2020 Dell Inc.
PPTX 2018.08.14

## Slide 17: Front End Bandwidth - MAA-VNX01
Copyright © 2020 Dell Inc.
PPTX 2018.08.14

## Slide 18: Front End IOPS vs Back End IOPS - MAA-VNX01
Copyright © 2020 Dell Inc.
PPTX 2018.08.14

## Slide 19: Top 3 Clients by IOPS - MAA-VNX01
Copyright © 2020 Dell Inc.
PPTX 2018.08.14

## Slide 20: Top 3 Clients by IOPS - MAA-VNX01
Client | #LUNs | Used (TB) | Peak IOPS | Response Time (ms) | Front End MB/sec | Read % | Avg IO Size (KB)
Celerra_MAA-CS0-VNX01 | 45 | 27 | 9,828 | 5.65 | 41 | 81.67% | 36.33
MAA-ESXi01.l1rtv.l1.nl MAA-ESXi02.l1rtv.l1.nl MAA-ESXi03.l1rtv.l1.nl MAA-ESXi06.l1rtv.l1.nl MAA-ESXi07.l1rtv.l1.nl MAA-ESXi08 MAA-ESXi09 MAA-ESXi10 | 5 | 8 | 5,243 | 31.99 | 28 | 38.98% | 41.29
MAA-ESXi04.l1rtv.l1.nl MAA-ESXi05.l1rtv.l1.nl | 3 | 1 | 2,960 | 2.7 | 6 | 66.55% | 24.38
PPTX 2018.08.14
Copyright © 2020 Dell Inc.

## Slide 21: IO Size and Read Percent - MAA-VNX01
Copyright © 2020 Dell Inc.
PPTX 2018.08.14

## Slide 22: IOPS Thresholds - MAA-VNX01
Copyright © 2020 Dell Inc.
PPTX 2018.08.14

## Slide 23: Back End Activity By Pool - MAA-VNX01
Copyright © 2020 Dell Inc.
PPTX 2018.08.14

## Slide 24: Back End Activity By Pool - MAA-VNX01
Copyright © 2020 Dell Inc.
PPTX 2018.08.14

## Slide 25: Back End Activity By Pool - MAA-VNX01
Copyright © 2020 Dell Inc.
PPTX 2018.08.14

## Slide 26: Total Queue Length - MAA-VNX01
Copyright © 2020 Dell Inc.
PPTX 2018.08.14

## Slide 27: Top Clients and LUNs

## Slide 28: Top 15 LUNs by IOPS - MAA-VNX01
LUN | Front End IOPS - max | Front End MB/sec-max | Avg IO Size (KB) | Latency (ms) - max | Latency (ms) - avg | Read % - avg
VMware-Productie_0 | 7,557 | 233 | 48.18 | 125.40 | 23.89 | 51.6%
LUN-File-NLSAS_16 | 5,365 | 150 | 29.7 | 27.30 | 2.04 | 97.34%
VMware-HorizonView_1 | 4,139 | 144 | 20.24 | 121.70 | 2.43 | 66.93%
LUN-File-NLSAS_15 | 3,619 | 72 | 42.33 | 24.90 | 2.77 | 85.59%
VMware-HorizonView_2 | 2,762 | 171 | 24.11 | 48.70 | 2.72 | 67.61%
VMware-Productie_2 | 2,399 | 88 | 20.18 | 176.50 | 30.40 | 17.7%
VMware-HorizonView_0 | 2,211 | 157 | 30.47 | 17.90 | 1.97 | 77.24%
VMware-Productie_1 | 1,973 | 66 | 31.61 | 528.50 | 49.02 | 30.98%
LUN-File-NLSAS_17 | 1,846 | 81 | 23.2 | 21.90 | 2.76 | 83.73%
LUN-File-NLSAS_18 | 1,681 | 82 | 24.18 | 23.50 | 3.12 | 88.23%
PPTX 2018.08.14
Copyright © 2020 Dell Inc.
Notes: This shows the top 15 LUNS by IOPS

## Slide 29: Top 15 LUNs by IOPS - MAA-VNX01
LUN | Front End IOPS - max | Front End MB/sec-max | Avg IO Size (KB) | Latency (ms) - max | Latency (ms) - avg | Read % - avg
LUN-File-NLSAS_20 | 1,584 | 81 | 26.26 | 21.20 | 2.60 | 88.59%
LUN-FIle-NLSAS_19 | 1,526 | 80 | 26.66 | 22.90 | 2.59 | 88.29%
LUN-File-NLSAS_6 | 1,509 | 21 | 17.95 | 55.30 | 3.64 | 84.94%
Lun-File-Mixed_17 | 1,355 | 158 | 133.62 | 130.50 | 16.85 | 79.36%
LUN-File-Mixed_3 | 1,220 | 57 | 50.05 | 214.10 | 5.63 | 69%
PPTX 2018.08.14
Copyright © 2020 Dell Inc.
Notes: This shows the top 15 LUNS by IOPS

## Slide 30: Top 15 LUNs by MBPS - MAA-VNX01
LUN | Front End IOPS - max | Front End MB/sec-max | Avg IO Size (KB) | Latency (ms) - max | Latency (ms) - avg | Read % - avg
VMware-Productie_0 | 7,557 | 233 | 48.18 | 125.40 | 23.89 | 51.6%
VMware-HorizonView_2 | 2,762 | 171 | 24.11 | 48.70 | 2.72 | 67.61%
Lun-File-Mixed_17 | 1,355 | 158 | 133.62 | 130.50 | 16.85 | 79.36%
VMware-HorizonView_0 | 2,211 | 157 | 30.47 | 17.90 | 1.97 | 77.24%
LUN-File-NLSAS_16 | 5,365 | 150 | 29.7 | 27.30 | 2.04 | 97.34%
VMware-HorizonView_1 | 4,139 | 144 | 20.24 | 121.70 | 2.43 | 66.93%
VMware-Productie_2 | 2,399 | 88 | 20.18 | 176.50 | 30.40 | 17.7%
LUN-File-NLSAS_18 | 1,681 | 82 | 24.18 | 23.50 | 3.12 | 88.23%
LUN-File-NLSAS_17 | 1,846 | 81 | 23.2 | 21.90 | 2.76 | 83.73%
LUN-File-NLSAS_20 | 1,584 | 81 | 26.26 | 21.20 | 2.60 | 88.59%
PPTX 2018.08.14
Copyright © 2020 Dell Inc.
Notes: This shows the top 15 LUNS by IOPS

## Slide 31: Top 15 LUNs by MBPS - MAA-VNX01
LUN | Front End IOPS - max | Front End MB/sec-max | Avg IO Size (KB) | Latency (ms) - max | Latency (ms) - avg | Read % - avg
LUN-FIle-NLSAS_19 | 1,526 | 80 | 26.66 | 22.90 | 2.59 | 88.29%
LUN-File-Mixed_16 | 1,173 | 80 | 74.2 | 123.10 | 20.15 | 73.95%
LUN-File-Mixed_14 | 1,134 | 80 | 81.35 | 103.90 | 19.91 | 74.61%
LUN-File-NLSAS_15 | 3,619 | 72 | 42.33 | 24.90 | 2.77 | 85.59%
VMware-Productie_1 | 1,973 | 66 | 31.61 | 528.50 | 49.02 | 30.98%
PPTX 2018.08.14
Copyright © 2020 Dell Inc.
Notes: This shows the top 15 LUNS by IOPS