## Slide 1: VNX Profile - MAA-VNX01
Project:
05/25/2020, 04:56 (UTC +02:00)
Demian Geven, demian.geven@l1.nl
1058182
VNX l1C
Project ID:
Prepared For:
Prepared By:
Created:
PPTX 2018.08.14
Copyright © 2020 Dell Inc.

## Slide 2: Common Summary: Inventory, Capacity and Workload
Serial No. | CKM00133700906
Model No. | VNX_5400
Software Level | 5.33.184
System Cache (GB) | 32
Fast Cache Enabled | True
Fast Cache (GB) | 275
Total No. Drives | 155
No. SSD Drives | 7
No. HDD Drives | 148
Usable SSD Capacity (TB) | 0.62
Usable HDD Capacity (TB) | 257.0
Subscription % | 93.67%
Subscription Capacity (TB) | 192.96
Used Capacity TB | 185.99
Configured Capacity (TB) | 205.78
LUN Skew - Avg IO | 83.7%
Configuration File Date | 2020-05-18
Performance Start | 2020-05-18 10:00:59
Performance End | 2020-05-25 00:34:36
Performance Interval | 1 mins
Peak IOPS: Date Time | 2020-05-19 12:55:37
Peak IOPS: IOPS | 12153
Peak IOPS: Read % | 80
Peak IOPS: Avg. Read Size (KB) | 13.66
Peak IOPS: Avg. Write Size (KB) | 38.93
Peak IOPS: MB/s | 221.32
Peak IOPS: Latency (ms) | 4.4
95th IOPS: Date Time | 2020-05-18 12:04:31
95th IOPS: IOPS | 8,229
95th IOPS: Read % | 81
95th IOPS: Avg. Read Size (KB) | 18.8
Inventory and Capacity Summary
Workload Summary Peak IOP Measurements
Workload Summary 95th Percentile Measurements
Workload Summary Peak MB/s Measurements
Peak MB/s: Date Time | 2020-05-19 12:05:50
Peak MB/s: IOPS | 6283
Peak MB/s: Read % | 78
Peak MB/s: Avg. Read Size (KB) | 56.76
Peak MB/s: Avg. Write Size (KB) | 189.57
Peak MB/s: MB/s | 525.17
Peak MB/s: Latency (ms) | 6.2
Copyright © 2020 Dell Inc.
PPTX 2018.08.14

## Slide 3: Summary - MAA-VNX01
Snap View | Yes
Mirror View | Yes
Recover Point | Yes
SAN Copy | Yes
Configuration File Date | 2020-05-18
Performance Start | 2020-05-18 10:01
Performance End | 2020-05-25 00:34
Performance Interval (mins) | 1 mins
FC 4GB | 0
FC 8GB | 4
FC 16GB | 0
1 GigE | 0
10 GigE | 0
iSCSI | 4
File | Yes
Block | Yes
Serial No. | CKM00133700906
Model No. | VNX_5400
Software Level | 5.33.184
System Cache (GB) | 32
No. DAEs | 9
Active Drives | 144
Inactive Drives | 11
Empty Slots | 10
Hardware Overview
Software Features
Input Data
Connectivity
Emulations
Copyright © 2020 Dell Inc.
PPTX 2018.08.14

## Slide 4: Capacity Summary by Drive Type - MAA-VNX01
Name | Model | Total Raw Capacity (TB) | Usable SSD (TB) | Configured Capacity (TB) | Used (TB) | Utilization (%)
MAA-VNX01 | VNX_5400 | 257.63 | 0.62 | 205.78 | 185.99 | 90
Drive Type | Rotational Speed (K) | Number of Spare Drive | Number of Data Drive | Raw Size (GB) | Number of Drives | Raw Capacity (TB) | Raw Capacity (%)
Unknown | Flash | 10 | 0 | 0 | 10 | 0.0 | 0.0
HDD | 7.2 | 3 | 80 | 2,751 | 83 | 222.98 | 86.55
HDD | 10 | 7 | 58 | 536 | 65 | 34.02 | 13.21
SSD | Flash | 1 | 6 | 91 | 7 | 0.62 | 0.24
Copyright © 2020 Dell Inc.
PPTX 2018.08.14
Notes: Utilization (%) is calculated by dividing Used(TB) by Usable (TB). Used/Usable * 100 = Utilization %

## Slide 5: Array Profile Metric - MAA-VNX01
Number of Disks | 155
Usable HDD (TB) | 257
Usable SSD (TB) | 0.62
Raw Capacity (TB) | 257.63
Used Capacity(TB) | 185.99
LUN Skew | 84% of IOPS/16% of LUNS
Front End MB/sec - max | 525
Date Time- Peak | 2020-05-19 12:55:37
IOPS at Peak | 12,153
Read % at Peak | 80.0
Read Size (KB) at Peak | 13.66
Write Size (KB) at Peak | 38.93
MB/sec at Peak | 221
Latency (ms) at Peak | 4.4
Copyright © 2020 Dell Inc.
PPTX 2018.08.14
Notes: SSD is the total RAW physical capacity of the array. LUN is the summation of the total volume size. LUN used is the amount of non-zero data written to the array before compression and deduplication. The rest measures a peak. This slide is designed to show in one slide all of the KPIs for sizing.

## Slide 6: 5 Year Growth Projection - MAA-VNX01
Copyright © 2020 Dell Inc.
At 20% growth, usable capacity will be exceeded in less than 1 year.
PPTX 2018.08.14

## Slide 7: Array Profile Details

## Slide 8: Array Capacity - MAA-VNX01
Copyright © 2020 Dell Inc.
PPTX 2018.08.14

## Slide 9: Fibre Channel Ports - MAA-VNX01
Name | Speed (Gbit/sec) | Read MB/sec 95th | Write MB/sec 95th
Port 0 [FC; 50:06:01:60:88:60:14:25:50:06:01:60:08:60:14:25 ] | 0 | 0 | 0
Port 0 [FC; 50:06:01:60:88:60:14:25:50:06:01:68:08:60:14:25 ] | 0 | 0 | 0
Port 1 [FC; 50:06:01:60:88:60:14:25:50:06:01:61:08:60:14:25 ] | 0 | 0 | 0
Port 1 [FC; 50:06:01:60:88:60:14:25:50:06:01:69:08:60:14:25 ] | 0 | 0 | 0
Port 2 [FC; 50:06:01:60:88:60:14:25:50:06:01:62:08:60:14:25 ] | 0 | 0 | 0
Port 2 [FC; 50:06:01:60:88:60:14:25:50:06:01:6A:08:60:14:25 ] | 0 | 0 | 0
Port 3 [FC; 50:06:01:60:88:60:14:25:50:06:01:63:08:60:14:25 ] | 0 | 0 | 0
Port 3 [FC; 50:06:01:60:88:60:14:25:50:06:01:6B:08:60:14:25 ] | 0 | 0 | 0
Port 4 [FC; 50:06:01:60:88:60:14:25:50:06:01:64:08:60:14:25 ] | 8 | 3 | 14
Port 4 [FC; 50:06:01:60:88:60:14:25:50:06:01:6C:08:60:14:25 ] | 8 | 32 | 31
Port 5 [FC; 50:06:01:60:88:60:14:25:50:06:01:65:08:60:14:25 ] | 8 | 0 | 1
Port 5 [FC; 50:06:01:60:88:60:14:25:50:06:01:6D:08:60:14:25 ] | 8 | 0 | 0
Copyright © 2020 Dell Inc.
PPTX 2018.08.14

## Slide 10: Fibre Channel Ports - MAA-VNX01
Name | Speed (Gbit/sec) | Read MB/sec 95th | Write MB/sec 95th
Port 6 [FC; 50:06:01:60:88:60:14:25:50:06:01:66:08:60:14:25 ] | 0 | 0 | 0
Port 6 [FC; 50:06:01:60:88:60:14:25:50:06:01:6E:08:60:14:25 ] | 0 | 0 | 0
Port 7 [FC; 50:06:01:60:88:60:14:25:50:06:01:67:08:60:14:25 ] | 0 | 0 | 0
Port 7 [FC; 50:06:01:60:88:60:14:25:50:06:01:6F:08:60:14:25 ] | 0 | 0 | 0
Port 8 [iSCSI; iqn.1992-04.com.emc:cx.ckm00133700906.a8 ] | 16 | 10 | 3
Port 8 [iSCSI; iqn.1992-04.com.emc:cx.ckm00133700906.b8 ] | 16 | 10 | 10
Port 9 [iSCSI; iqn.1992-04.com.emc:cx.ckm00133700906.a9 ] | 16 | 10 | 3
Port 9 [iSCSI; iqn.1992-04.com.emc:cx.ckm00133700906.b9 ] | 16 | 10 | 10
Copyright © 2020 Dell Inc.
PPTX 2018.08.14

## Slide 11: Performance Profile - MAA-VNX01
Copyright © 2020 Dell Inc.
PPTX 2018.08.14

## Slide 12: Front End Ports: Peak Composite
Copyright © 2019 Dell Inc.
Chart: 
26-69% | 26
70-89%
90-100%
Chart: 
26-69% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70-89% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
90-100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Slide 13: Cache Utilization
SP-B
Chart: Cache Flush (MB/s)
Chart: Cache Flush (MB/s)
Copyright © 2019 Dell Inc.
SP-A

## Slide 14: Peak/Average Ports Utilization
Chart: 
| SPA 4 | SPA 5 | SPA 8 | SPA 9
Peak 0-25% | 22 | 8 | 8 | 8
Peak 26-69%
Peak 70-89%
Peak 90-100%
Average 0-25% | 2 | 0 | 0 | 0
Average 26-69%
Average 70-89%
Average 90-100%
Baseline | 0 | 0 | 0 | 0
Peak Timestamp
Chart: 
| SPB 4 | SPB 5 | SPB 8 | SPB 9
Peak 0-25% | 0 | 23 | 20
Peak 26-69% | 26
Peak 70-89%
Peak 90-100%
Average 0-25% | 2 | 0 | 1 | 1
Average 26-69%
Average 70-89%
Average 90-100%
Baseline | 0 | 0 | 0 | 0
Peak Timestamp
Copyright © 2019 Dell Inc.
Peak Utilization
Average Utilization
Notes: FE Port Utilization – Avg/Peak

## Slide 15: Storage Processor Utilization
Copyright © 2020 Dell Inc.
PPTX 2018.08.14

## Slide 16: Front End Latency - MAA-VNX01
Copyright © 2020 Dell Inc.
PPTX 2018.08.14

## Slide 17: Front End Bandwidth - MAA-VNX01
Copyright © 2020 Dell Inc.
PPTX 2018.08.14

## Slide 18: Front End IOPS vs Back End IOPS - MAA-VNX01
Copyright © 2020 Dell Inc.
PPTX 2018.08.14

## Slide 19: Top 3 Clients by IOPS - MAA-VNX01
Copyright © 2020 Dell Inc.
PPTX 2018.08.14

## Slide 20: Top 3 Clients by IOPS - MAA-VNX01
Client | #LUNs | Used (TB) | Peak IOPS | Response Time (ms) | Front End MB/sec | Read % | Avg IO Size (KB)
Celerra_MAA-CS0-VNX01 | 45 | 27.05 | 8,967 | 5.84 | 39 | 84.23% | 30.64
MAA-ESXi01.l1rtv.l1.nl MAA-ESXi02.l1rtv.l1.nl MAA-ESXi03.l1rtv.l1.nl MAA-ESXi06.l1rtv.l1.nl MAA-ESXi07.l1rtv.l1.nl MAA-ESXi08 MAA-ESXi09 MAA-ESXi10 | 5 | 8.01 | 4,132 | 16.02 | 35 | 48.14% | 28.25
MAA-ESXi04.l1rtv.l1.nl MAA-ESXi05.l1rtv.l1.nl | 3 | 0.88 | 2,734 | 3.04 | 10 | 67.89% | 26.14
PPTX 2018.08.14
Copyright © 2020 Dell Inc.

## Slide 21: IO Size and Read Percent - MAA-VNX01
Copyright © 2020 Dell Inc.
PPTX 2018.08.14

## Slide 22: IOPS Thresholds - MAA-VNX01
Copyright © 2020 Dell Inc.
PPTX 2018.08.14

## Slide 23: Back End Activity By Pool - MAA-VNX01
Copyright © 2020 Dell Inc.
PPTX 2018.08.14

## Slide 24: Back End Activity By Pool - MAA-VNX01
Copyright © 2020 Dell Inc.
PPTX 2018.08.14

## Slide 25: Back End Activity By Pool - MAA-VNX01
Copyright © 2020 Dell Inc.
PPTX 2018.08.14

## Slide 26: Total Queue Length - MAA-VNX01
Copyright © 2020 Dell Inc.
PPTX 2018.08.14

## Slide 27: Top Clients and LUNs

## Slide 28: Top 15 LUNs by IOPS - MAA-VNX01
LUN | Front End IOPS - max | Front End MB/sec-max | Avg IO Size (KB) | Latency (ms) - max | Latency (ms) - avg | Read % - avg
VMware-Productie_0 | 5,433 | 184 | 26.64 | 107.60 | 7.14 | 59%
LUN-File-NLSAS_16 | 3,725 | 111 | 37.05 | 21.80 | 1.89 | 96.59%
VMware-Productie_2 | 2,667 | 370 | 19.78 | 114.30 | 27.33 | 25.89%
VMware-HorizonView_2 | 2,632 | 127 | 21.14 | 589.20 | 2.82 | 61.88%
VMware-HorizonView_1 | 2,366 | 109 | 22.16 | 41.60 | 2.59 | 67.97%
LUN-File-Mixed_16 | 1,776 | 65 | 64.2 | 183.90 | 15.63 | 80.8%
LUN-File-Mixed_14 | 1,747 | 64 | 69.12 | 211.70 | 13.55 | 82.3%
VMware-HorizonView_0 | 1,658 | 108 | 29.14 | 30.30 | 2.48 | 70.02%
LUN-FIle-NLSAS_19 | 1,568 | 39 | 23 | 13.90 | 3.00 | 90.47%
LUN-File-NLSAS_17 | 1,549 | 39 | 24.94 | 11.50 | 2.26 | 79.93%
PPTX 2018.08.14
Copyright © 2020 Dell Inc.
Notes: This shows the top 15 LUNS by IOPS

## Slide 29: Top 15 LUNs by IOPS - MAA-VNX01
LUN | Front End IOPS - max | Front End MB/sec-max | Avg IO Size (KB) | Latency (ms) - max | Latency (ms) - avg | Read % - avg
LUN-File-Mixed_2 | 1,538 | 51 | 26.91 | 67.00 | 5.08 | 83.7%
VMware-Productie_1 | 1,477 | 65 | 36.9 | 300.30 | 69.65 | 30.31%
LUN-File-Mixed_5 | 1,425 | 51 | 26.55 | 61.70 | 4.81 | 84.14%
LUN-File-Mixed_0 | 1,396 | 52 | 27.19 | 56.40 | 4.98 | 84.38%
LUN-File-NLSAS_18 | 1,384 | 39 | 25.43 | 23.00 | 2.81 | 86.36%
PPTX 2018.08.14
Copyright © 2020 Dell Inc.
Notes: This shows the top 15 LUNS by IOPS

## Slide 30: Top 15 LUNs by MBPS - MAA-VNX01
LUN | Front End IOPS - max | Front End MB/sec-max | Avg IO Size (KB) | Latency (ms) - max | Latency (ms) - avg | Read % - avg
VMware-Productie_2 | 2,667 | 370 | 19.78 | 114.30 | 27.33 | 25.89%
VMware-Productie_0 | 5,433 | 184 | 26.64 | 107.60 | 7.14 | 59%
VMware-HorizonView_2 | 2,632 | 127 | 21.14 | 589.20 | 2.82 | 61.88%
LUN-File-NLSAS_16 | 3,725 | 111 | 37.05 | 21.80 | 1.89 | 96.59%
VMware-HorizonView_1 | 2,366 | 109 | 22.16 | 41.60 | 2.59 | 67.97%
Lun-File-Mixed_17 | 729 | 109 | 131.64 | 164.60 | 19.34 | 75.63%
VMware-HorizonView_0 | 1,658 | 108 | 29.14 | 30.30 | 2.48 | 70.02%
VMware-Productie_1 | 1,477 | 65 | 36.9 | 300.30 | 69.65 | 30.31%
LUN-File-Mixed_16 | 1,776 | 65 | 64.2 | 183.90 | 15.63 | 80.8%
LUN-File-Mixed_14 | 1,747 | 64 | 69.12 | 211.70 | 13.55 | 82.3%
PPTX 2018.08.14
Copyright © 2020 Dell Inc.
Notes: This shows the top 15 LUNS by IOPS

## Slide 31: Top 15 LUNs by MBPS - MAA-VNX01
LUN | Front End IOPS - max | Front End MB/sec-max | Avg IO Size (KB) | Latency (ms) - max | Latency (ms) - avg | Read % - avg
LUN-File-NLSAS_15 | 449 | 64 | 89.54 | 29.70 | 3.88 | 77.02%
LUN-File-Mixed_0 | 1,396 | 52 | 27.19 | 56.40 | 4.98 | 84.38%
LUN-File-Mixed_3 | 1,382 | 51 | 28.4 | 51.80 | 4.65 | 83.1%
LUN-File-Mixed_2 | 1,538 | 51 | 26.91 | 67.00 | 5.08 | 83.7%
LUN-File-Mixed_1 | 1,312 | 51 | 27.81 | 60.80 | 4.77 | 83.69%
PPTX 2018.08.14
Copyright © 2020 Dell Inc.
Notes: This shows the top 15 LUNS by IOPS