Use case 11.1

Emergency Situations – Fire Alarms

# In scope

| Naam (Name) | 11.1 -- Emergency Situations - Fire Alarm. |
| --- | --- |
| Samenvatting / Description | A fire alarm will be send to the BHV group and to additional emergency response to follow up the alarm generated by the fire detection system. |
| Actoren / Actors | Emergency response team |
| Aannamen / Triggers | In the complete hospital a fire detection system is installed in line with regulation. |
| Customer user stories | RSA-B01 |
| System functions involved | - Fire detection system - Building management systeem - Communication platform fulfilling NEN 2575(PZI installatie) |
| System Beschrijving / Description | This case is describing the communication at a fire alarm assuming that the wish of the user is silent alarming in case of a detected fire. Starting point of this use case: Accourding to NEN 2575 a compliant paging system is needed. This means in this use case that the pager is seen as mandatory primary route to a fixed group of users . A fire detection system is installed in the complete hospital. Fire is automaticly detected and with manual fire alarm buttons, like in the picture below, also an alarm can be triggered. The intelligence of alarm handling is foreseen to be present in the RMTS. The Fire detections system gives a trigger at alarm and preferred a cancel at reset. At an automatic or manual alarm the alarm information is forwarded to the Emergency response team for fire. This is a group of employees with the right skills and responsibility to handle this calamity. According to the NEN2575 norm it is only allowed to send the alarm to the group of BHV people automatically! In the message send to this team minimum the location and type of alarm is presented in a clear, non-interpretable way. If the receiving device is capable of sending information back an acknowledge or reject can be send by each and every team member. In this way the porter/head BHV can check if the minimum amount of responder has been achieved. If this is not the case a back-up scenario can be (automatically) initiated. |
| Non-functional requirements (quality aspect) |  |
| Starting points Preconditions Points for attention System | - The fire system is connected to the RTMS. This can be direct or via the building management system. Option: - Messaging to Myco’s is possible as secondary route - The NEN2575 fire alarming system is a separate paging system with its own UCM. User management will be done/can be done via Unite AM of the RTMS - Processes are in place for the Emergency reponse team for Fire |
| Uitzonderingen / Exceptions |  |
| Issues | The way of connecting the fire detection systems and RTMS has not yet be defined. his use case is written with the default setting of the system in mind. |