## Questionnaire
Format fot general inquiries
| Project: | Market consultation SCADA Operational System 2026 - 2040
| Date: | 2025-05-16
| Version: | 1
collected list
Nr | Chapter | Question interested party | Response | Changed document
1 | General | Can you share the architecture proposed by the government based on open standards and open source? | ProRail follows NORA (https://www.noraonline.nl).
2 | General | Do you have or foresee any limitation regarding cloud usage? Public vs. private cloud? | ProRail has no prejudiced opinion on cloud solutions. The option to use (a) cloud solution(s) will be dependent on the possibilities to realise all functional and non-functional requirements. The FR/NFR package will be made available during the tender.
3 | General | Are all existing SCADA systems from same vendor? | No, ProRail makes use of multiple SCADA solutions and vendors.
4 | General | In terms of track maintenance, what are the processes and activities established by ProRail Management to meet asset management objectives? | The new system influences the primary KPI (track availability) by seamless integration with the operational processes.
5 | General | What are the key performance indicators (KPIs) considered until the present time to assess the actual system's impact on track maintenance outcomes? | The primary KPI is track availability. All other KPI's are derived from or based on this. Due to the variety of domains (EV, movable bridges, tunnels, etc.) derived KPIs can be conflicting.
6 | General | What specific track maintenance tasks and activities will the system facilitate or optimize? | The required functionality of the new system is described in par. 2.3, specifically the points 4,5,6.
7 | General | Subchapter 2.2 mentions the monitoring of railway lines to ensure track stability. Given that deviations can occur due to various factors and indicate potential problems that need to be addressed to maintain the integrity of railway tracks, it would be useful to know what is being monitored: track geometry, defects in track superstructure elements (rail, fastenings, sleepers, etc.), ballast condition, track bed condition, environmental factors that can influence track stability such as temperature of rail? | ProRail uses a variety of solutions to monitor the suggested signals. These solutions will not be part of the system scope. However the system will need to be able to integrate with those monitoring solutions by means of APIs. The most obvious usecase is to ingest the alarms of these monitoring solutions.
8 | General | What monitoring systems are used to provide the information needed for continuous monitoring of the condition of railway tracks to adopt proactive maintenance? | ProRail uses a variety of solutions to monitor maintenance indicators. If (and only if) these solutions are going to be integrated into the new system, they will use standard protocols such as IEC104, OPC UA and REST.
9 | 2.3 Architecture | Is there an AS-IS architecture that could be shared? Single line architectures / general architectures. | No. Current architectures are tailor made for their purpose. They could potentially be made available during the tender, if this is beneficial for the tender process.
10 | 2.3 Architecture | How much control is required? Full control ? | The level of control is dependent on the asset type and the operational processes interacting with that asset. There are as many levels of control as there are asset types and processes.
11 | 2.3 Architecture | If full control is required, how will 2 operators manage the system from the Centralized and Local SCADA? | The new system needs to facilitate both local and central operation in which conflicts are handled based on safety, role and business process requirements.
12 | 2.3 Architecture | Is there a request also for high availability / redundancy /seamless failover / failover Clusters? | Yes. However, HA/FO will only be needed in operationally critical domains, such as EV and tunnels.
13 | 2.3 Architecture | All SCADA have the same architecture? | No. The current SCADA solutions are specifically designed for their primary domains: (EV, tunnels, bridges, etc) based upon tailor made architectures.
14 | 2.3 Architecture | Central Service Desk, offering 24/7 incident support - Is this integrated in the SCADA architecture or is it a separate app/service? | The CSD is a separate service. Authorized staff currently have limited access to certain asset domains and functionalities.
15 | 2.3 Architecture | Preparing, simulating and executing switching operations . Is this simulation built into the existing SCADA systems or PLC level or other SIM environment? | It is part of the existing SCADA system.
16 | 2.3 Architecture | Ability to remotely apply software blocks on switches. Could you please provide more details (is there a dev environment? What if switches are active while block download?)? | For certain safety critical applications (such as EV) it is paramount to be to able to block remote activation of switches. These blocks need to be implemented by the new system as an application function.
17 | 2.3 Architecture | Display of schematic and geographical information at different levels.IS there a GIS Server operation? | ProRail does utilize own GIS functionality for certain business questions. We could also allow GIS application for the new system if geography is a useful operational aspect. However such a benefit has not yet been identified. We expect schematic or symbolic representation to suffice.
18 | Networking | Redundant network in case of disconnect? | Where needed ProRail provides redundant networks and/or communication paths between systems.
19 | Networking | Wireless communication? If yes, what protocols (GPRS, Radio, Satellite)? | 4G, GSM-R, WiFi.
20 | Networking | What types of RTUs are available? | ProRail uses a variety of analog and digital RTUs.
21 | Networking | Data is also stored in historian? - If yes, for what period should the data be stored? - How many datapoints approximately? | Yes. The size of the historical period is dependent on business needs and legal mandates. It varies from days to years. "Hard" data points, such as sensor values will be short lived, whereas safety related data points, such as the activation of an electrical switch, will require a retention of more than a decade. The amount of datapoints has not yet been estimated.
22 | Networking | Support of switching order processes for ProRail and contractors. - Using what interface? - Ability to perform data engineering changes without impacting monitoring and operation - How is it done now? | - The new system must provide an MMI to support the creation, verification and execution of switching orders. This functionality must be available for both ProRail and contractors. - Currently data engineering changes are prepared offline, putting them into operations (online). This is noticed by the users only by a short black screen.
23 | Networking | Limited alignment with the architecture proposed by the government based on open standards and open source code can lead to compatibility problems and non-compliance with guidelines in the future. • Is open architecture allowed? Ex. Commercial software with DBs open to access by developers. | Yes.
24 | Networking | Are there OS limitations? Run on Windows, Linux, Virtual Environments? | There are no OS limitations.
25 | Networking | Docker containers and Kubernetes would be an option? | Yes.
26 | Networking | Is it required that the UI screens automatically reorganize based on the screen resolution or device type? | Preferably yes for the resolution. No for the device type.
27 | Networking | Will the screens also be used/accessed on tablets and/or phones? | ProRail is aiming to facilitate device independent access. However this is heavily influenced by aspects such as domain (EV, bridges, tunnels, etc), application functionality and cyber security. If and when possible applications should be device independent, or provide a suitable specific MMI.
28 | Networking | Is there any part of the old SCADA system that can be/should be reused in the new system? | The new system needs be able to integrate with existing systems. Integration will be based upon standard protocols (such as IEC104, OPC UA, REST, Modbus, MQTT). Certain asset domains (such as tunnels and bridges) are complex. They are a little eco system in themselves. These environments will require risk averse integration and migration strategies.
29 | Networking | Can protocol adapters / gateways be leveraged in order to communicate with PLC/RTUs? | Yes.
30 | 2.2 | Is the list of assets complete or is there a chance that it will be expanded? | The list of assets is pretty stable, but not fixed. As a natural part of technology evolution and changed business needs the list of assets will evolve as well
31 | 1.3 | Is the scope a 1-on-1 replacement of the Scada systems or can/must adjustments also be made at interfaces (such as the connections to the assets)? | We expect to need a 1:1 replacement.
32 | 4.3 | What will be part of the tender procedure? (design, design and construction, maintenance, client consultation, other?) | In essence ProRail is only providing the specifications. ProRail will provide a requirements package. This package comprises a reference architecture, system capabilities, FRs/NFRs, business needs (support, maintenance, training, etc), legal constraints and technical limitations. This specification will be driver of the tender.
33 | 4.3 | To what extent are (design) regulations expected to be adjusted/made as a result of this project? | The application landscape within ProRail is shaped by reference architectures, information security policies and other specifications. Given sufficient benefit ProRail could potentially allow extensions to, or modifications of the current frameworks.
34 | 2.4 | Is cyber security part of the scope? If so, is the IEC62443 series leading and is the NVN-CLCTS 50701 - CS rail in effect? | Yes and yes.
35 | 2.4 | Has ProRail thought about the phasing of the implementation (per system, per area, other?) | Yes. We expect this to be part of the migration strategy. This is hinted at in par. 3.3 "Migratie en beheerinchting".
36 | General | On a scale of 1 to 10, how important is it for your organization to have fast and effective technical support to resolve any issues related to the SCADA/MES/MOM system?(1 = Not important at all, 10 = Extremely important) | The required support is very much depending on the robustness and resilience of the system, in combination with asset domain and the functionality of subsystems.
37 | General | How satisfied are you currently with the level of support and maintenance you receive for your SCADA/MES/MOM system? (1 = Very dissatisfied, 10 = Very satisfied) | ProRail does not discuss relationships with business partners.
38 | General | How critical is it for your operation to have access to regular software updates and security patches for the SCADA/MES/MOM system? (1 = Not critical at all, 10 = Extremely critical) | The required support is very much depending on the robustness and resilience of the system, in combination with asset domain and the functionality of that subsystem.
39 | General | • On a scale of 1 to 10, how much do you value the availability of preventive maintenance services to ensure optimal performance and continuous reliability of the SCADA/MES/MOM system? (1 = Do not value at all, 10 = Highly value) | The required support is very much depending on the robustness and resilience of the system, in combination with asset domain and the functionality of subsystems.
40 | General | How important is it for your organization to have a clear and well-defined service support contract with the SCADA/MES/MOM system provider? (1 = Not important at all, 10 = Extremely important) | The required support is very much depending on the robustness and resilience of the system, in combination with asset domain and the functionality of subsystems. The level of support will be clearly defined in an SLA
41 | General | Is there currently a PLM service in place at ProRail? Change Management support? After Sales support? | ProRail does not discuss commercial relationships with business partners.
42 | 1.3 Scope | "According to Chapter 1.3 Scope, "ProRail is looking for an integrated solution for monitoring, monitoring and operating railway assets through SCADA functionality". Can ProRail clarify whether interlocking and level crossings are excluded under 'operating railway assets', because these assets must comply with SIL4?" | The current SCADA system is not SIL compliant. We do not expect this to be a requirement for the new system, as this is delegated to other systems and parts of the organisation.
43 | 2.3 Architecture | Can ProRail provide a more detailed explanation of what ProRail understands by the software blocks on switches in the energy supply system as mentioned in point 5 of this paragraph? | For certain safety critical applications (such as EV) it is paramount to be to able to block remote activation of switches. These blocks need to be implemented by the new system as an application function.
44 | 2.3 Architecture | "Can ProRail provide a detailed explanation of point 6? Point 6: Does ProRail refer to a contract management function?" | 1. Contractor describes the location where he needs to work and which groups need to be switched off. 2. Operator checks the description and creates a switching sequence for turning off the selected groups. 3. Operator approves the sequence. 4. When the contractor starts working he calls the operator and the operator executes the sequence.
45 | General | Can ProRail provide an estimate of how many tags / notifications can be expected per (part) system that need to be integrated into the overall system? | This will be clarified during the tender.
46 | General | In addition to supplying the software solution, does the possible tender also include replacing the hardware and cabling of the various subsystems? | Yes, but within the scope of the actual system, thus excluding the assets.
47 | General | Some time ago there was a market consultation for remote access monitoring. The intention is that the functionality of this remote access monitoring will also be introduced into this SCADA system. | No.
48 | General | Is there already a vision of where this solution should be hosted (locally or in the cloud) and what reasons are there for a particular choice? | ProRail has no prejudiced opinion on cloud or on-prem solutions. The option to use these environment will be dependent on the possibilities to realise all functional and non-functional requirements. The FR/NFR package will be made available during the tender.
49 | General | Is ProRail looking for an integrated, overarching solution, or are separate solutions per subject/area an option? | ProRail is looking for an integral solution, comprising subsystems, modules and/or solutions. The various elements should follow MACH principles to allow for flexibility and technology independence.
50 | General | Are notifications and logging stored as part of the solution, or does ProRail already have solutions for this in use? | Logging and/or notifications are expected to be part of the system. They are in scope.
51 | 3.3 Migration and management setup - QUESTION 5. In your opinion, what does the ideal management and development setup look like for both the supplier and the client? | Regarding question 5 of the questionnaire: "In your opinion, what does the ideal management and development setup look like for both the supplier and the client?" 🡪 Can we assume that this means our contractual relationship with our clients during the implementation, as well as in regard to support. Can you confirm? | In question 5, ProRail is the client and you are the supplier. The tender will include (at least) implementation and support. Further details will be provided during the tender.