## Data summary
Foundation properties
Identification |  |  | Wind farm 2
Turbine | Rated power | [MW] | 9.5
| Nacelle plus rotor mass | [tonnes] | 478.4
| Hub height | [m LAT] | 108.85
| Rotor diameter [m] | [m] | 164
| Lower position of blade tip | [m LAT] | 26.85
Tower | Top elevation | [m LAT] | 105.81
| Bottom elevation | [m LAT] | 19.15
| Top diameter | [mm] | 4530
| Bottom diameter | [mm] | 6500
| Maximum wall thickness | [mm] | 37
| Minimum wall thickness | [mm] | 16
| Steel quality |  | S355
Transition piece | Top elevation | [m LAT] | --
| Bottom elevation | [m LAT] | --
| Top diameter | [mm] | --
| Bottom diameter | [mm] | --
| Maximum wall thickness | [mm] | --
| Minimum wall thickness | [mm] | --
| Main platform | [m LAT] | 18.5
| Steel quality |  | --
Pile | Top elevation | [m LAT] | 19.15
| Bottom elevation | [m LAT] | -63.35
| Top diameter | [mm] | 6500
| Mudline diameter | [mm] | 7400
| Maximum wall thickness | [mm] | 88
| Minimum wall thickness | [mm] | 62
| Water depth | [m] | 34.6
| Pile penetration | [m] | 28.75
| Steel quality |  | S275 / S355
Water level | MSL | [m LAT] | 1.72

## Wind farm 2 Data
Technical information Windfarm 2, Location 'WD 34.6m / PD 28.75m' (anonymized)
1. The Rotor-Nacelle Assembly (RNA) |  |  | General set-up and nomenclature tower
a) Turbine | 9.5 MW
b) Hub height | 108.85 | [mLAT]
c) Rotor diameter | 164 | [m]
d) Blade length | -- | [m]
e) Rotor mass (hub + 3 blades) | 184.502 | [tonne]
f) Nacelle mass | 293.882 | [tonne]
g) Total mass nacelle + rotor | 478.384 | [tonne]
n) Centre of Gravity (COG) nacelle + rotor
XHVR (fore-aft) = | 0 | [m]
YHVR (transverse) = | -0.78112 | [m]
ZHVR (vertical) = | 108.0452 | [mLAT]
o) Mass moment of inertia nacelle + rotor (wrt. COG)
Ixx = | 52610684.7896 | [kg m^2]
Iyy = | 96182584.6531 | [kg m^2]
Izz = | 52808100.1365 | [kg m^2]
2. Miscellaneous Design properties
a) Design Lifetime | 25 | [yrs]
b) Distance Tower top - Hub height | 3.04 | [m]
c) Position top of flange Tower | 105.81 | [mLAT]
d) Lower position of blade tip | 26.85 | [mLAT]
e) Position top of flange MP | 19.15 | [mLAT]
e) Factor on the density to model the Tower internals | 1.103 | [-]
Coordinate system
3. Water levels
MSL | 1.72 | [mLAT]
HAT | 3.78 | [mLAT]
EHWL1yr | 4.43 | [mLAT]
ELWL1yr | -0.38 | [mLAT]
EHWL50yr | 5.2 | [mLAT]
ELWL50yr | -0.86 | [mLAT]
DWL | 5.38 | [mLAT]
MWL | 1.89 | [mLAT]
3. Tower added masses
| Distance from | Mass
LAT
| [m] | [kg]
Damper | 99.63 | 25000
PCM | 33.13 | 55000
Tower internals | 105.58 | 3.6108
| 105.48 | 27.4387
| 104.49 | 61.0713
| 80.43 | 88.4397
| 77.7 | 93.1332
| 74.97 | 97.0965
| 72.01 | 97.0638
| 69.41 | 104.8719
| 66.71 | 108.6493
| 38.49 | 149.7667
| 35.71 | 139.0028
| 33.13 | 143.8836
| 30.51 | 148.6269
| 27.95 | 114.9979
| 26.45 | 166.3637
| 24.28 | 165.597
| 22.12 | 166.3637
| 19.95 | 47.5325
Total mass |  | 83718.8493
4. Pile added masses
| Distance from | Mass
LAT
| [m] | [kg]
Main Platform | 18.5 | 15000
Hang-off platform | 17.95 | 6500
Upper ladder | 14 | 3000
Boatlanding + ladder | 4.5 | 20000
Total mass |  | 44500
5. Tower layout
Segment | Position | Position | Shell | Shell | Shell | Shell | Material | Mass
number | top of shell | top of shell | height | OD top | OD bottom | thickness
[#] | [mmLAT] | [mLAT] | [mm] | [mm] | [mm] | [mm] |  | [kg]
1 | 105810 | 105.81 | 130 | 4605 | 4530 | 109.3 | S355 | 1562.2214 | Flange
2 | 105680 | 105.68 | 100 | 4530 | 4530 | 25 | S355 | 277.7502
3 | 105580 | 105.58 | 100 | 4530 | 4530 | 25 | S355 | 277.7502
4 | 105480 | 105.48 | 760 | 4530 | 4529 | 25 | S355 | 2110.667
5 | 104720 | 104.72 | 30 | 4529 | 4529 | 24 | S355 | 79.992 | Flange
6 | 104690 | 104.69 | 80 | 4529 | 4529 | 161 | S355 | 1387.4522
7 | 104610 | 104.61 | 90 | 4529 | 4529 | 170.3 | S355 | 1647.5313 | Flange
8 | 104520 | 104.52 | 30 | 4529 | 4525 | 24 | S355 | 79.9565
9 | 104490 | 104.49 | 2100 | 4525 | 4586 | 20 | S355 | 4697.7942
10
11
12
13
14
15
16
17
18 | 80430 | 80.43 | 2730 | 5267 | 5352 | 19.1 | S355 | 6803.0561
19 | 77700 | 77.7 | 2730 | 5352 | 5436 | 19.8 | S355 | 7164.0926
20 | 74970 | 74.97 | 2720 | 5436 | 5521 | 20.4 | S355 | 7468.9592
21 | 72250 | 72.25 | 30 | 5521 | 5521 | 21 | S355 | 85.4521 | Flange
22 | 72220 | 72.22 | 90 | 5521 | 5521 | 224.8 | S355 | 2642.547
23 | 72130 | 72.13 | 90 | 5521 | 5521 | 224.8 | S355 | 2642.547 | Flange
24 | 72040 | 72.04 | 30 | 5521 | 5521 | 21 | S355 | 85.4521
25 | 72010 | 72.01 | 2600 | 5521 | 5611 | 21 | S355 | 7466.4425
26 | 69410 | 69.41 | 2700 | 5611 | 5702 | 21.5 | S355 | 8067.0672
27
28
29
30
31
32
33
34 | 48290 | 48.29 | 2300 | 6333 | 6411 | 24.7 | S355 | 8892.6939
35 | 45990 | 45.99 | 2270 | 6411 | 6489 | 25 | S355 | 8992.0462
36 | 43720 | 43.72 | 40 | 6489 | 6489 | 26 | S355 | 165.7628 | Flange
37 | 43680 | 43.68 | 110 | 6489 | 6489 | 227.5 | S355 | 3864.3104
38 | 43570 | 43.57 | 110 | 6489 | 6489 | 227.5 | S355 | 3864.3104 | Flange
39 | 43460 | 43.46 | 40 | 6489 | 6489 | 26 | S355 | 165.7628
40 | 43420 | 43.42 | 2000 | 6489 | 6489 | 26 | S355 | 8288.1391
41
42
43
44
45
46
47
48
49 | 22120 | 22.12 | 2170 | 6500 | 6500 | 37 | S355 | 12797.2055
50 | 19950 | 19.95 | 620 | 6500 | 6500 | 37 | S355 | 3656.3444
51 | 19330 | 19.33 | 40 | 6500 | 6500 | 37 | S355 | 235.8932 | Flange
52 | 19290 | 19.29 | 140 | 6500 | 6500 | 245 | S355 | 5291.039
53 | 19150 | 19.15
Total mass | [7 empty] | 310143.3087
7. Pile layout Pile 'WD 34.6m / PD 28.75m' (Large water depth)
Seabed level: | -34.6 | [mLAT]
Penetration level: | -63.35 | [mLAT]
Penetration depth: | 28.75 | [m]
Pile layout 'WD 34.6m / PD 28.75m' (heaviest/longest pile)
Segment | Position | Position | Shell | Shell | Shell | Shell | Material | Mass
number | top of shell | top of shell | height | OD top | OD bottom | thickness
[#] | [mmLAT] | [mLAT] | [mm] | [mm] | [mm] | [mm] |  | [kg]
1 | 19150 | 19.15 | 175 | 6500 | 6500 | 215 | S355 | 5831.7825 | Flange
2 | 18975 | 18.975 | 50 | 6500 | 6500 | 69 | S355 | 547.1635
3 | 18925 | 18.925 | 11565 | 6500 | 6500 | 69 | S355 | 126558.922
4
5
6
7
8
9
10
11
12 | -24000 | -24 | 3300 | 7400 | 7400 | 67 | S275 | 39984.3423
13
14
15
16
17 | -61350 | -61.35 | 2000 | 7400 | 7400 | 77 | S275 | 27811.812
18 | -63350 | -63.35 | 0 | 7400 | 7400 | 77 | S275 | 0
Total mass | [7 empty] | 967504.0874

## Wind farm 2 Loads
Technical information Windfarm 2 (anonymized)
Location: 'WD 34.6m / PD 28.75m'
| Applied load |  | Total load in cross-section
| Position | Horizontal | Position | Shear | Bending
Nr | Height | Force | Height | Force | Moment
| [mm] | [N] | [m] | [kN] | [kNm]
Hub height | 108900 | 525081.4023 | 108.9 | 525.0814 | 0
1 | 105810 | 0 | 105.81 | 525.0814 | 1622.5015 | Flange
2
3 | 105580 | 123.8672 | 105.58 | 0.12387 | 0
4 | 105480 | 532.5943 | 105.48 | 0.65646 | 0.012387
5 | 104720 | 489.202 | 104.72 | 1.1457 | 0.5113 | Flange
6
7 | 104610 | 105.2639 | 104.61 | 0.10526 | 0 | Flange
8 | 104520 | 74.2984 | 104.52 | 0.17956 | 0.0094737
9 | 104490 | 1323.5729 | 104.49 | 1.5031 | 0.014861
10 | 102390 | 3052.0355 | 102.39 | 4.5552 | 3.1714
11
12
13
14
15
16
17
18
19 | 77700 | 3995.06 | 77.7 | 3.9951 | 0
20 | 74970 | 4050.5427 | 74.97 | 8.0456 | 10.9065
21 | 72250 | 2065.2301 | 72.25 | 10.1108 | 32.7906 | Flange
22 | 72220 | 90.5789 | 72.22 | 10.2014 | 33.0939
23 | 72130 | 135.8684 | 72.13 | 10.3373 | 34.012 | Flange
24 | 72040 | 90.5789 | 72.04 | 10.4279 | 34.9424
25 | 72010 | 1995.8518 | 72.01 | 12.4237 | 35.2552
26 | 69410 | 4066.3164 | 69.41 | 16.49 | 67.5568
27 | 66710 | 4202.0877 | 66.71 | 20.6921 | 112.0799
28 | 64020 | 4254.2846 | 64.02 | 24.9464 | 167.7417
29 | 61340 | 4321.5457 | 61.34 | 29.2679 | 234.5981
30 | 58650 | 4388.8842 | 58.65 | 33.6568 | 313.3288
31 | 55970 | 4439.7094 | 55.97 | 38.0965 | 403.5291
32 | 53300 | 4506.476 | 53.3 | 42.603 | 505.2469
33 | 50620 | 4279.8624 | 50.62 | 46.8829 | 619.423
34 | 48290 | 4008.4133 | 48.29 | 50.8913 | 728.6601
35 | 45990 | 4005.5162 | 45.99 | 54.8968 | 845.71
36 | 43720 | 2041.2889 | 43.72 | 56.9381 | 970.3258 | Flange
37 | 43680 | 133.0752 | 43.68 | 57.0712 | 972.6033
38 | 43570 | 195.177 | 43.57 | 57.2663 | 978.8811 | Flange
39 | 43460 | 133.0752 | 43.46 | 57.3994 | 985.1804
40 | 43420 | 1809.8227 | 43.42 | 59.2092 | 987.4764
41 | 41420 | 4373.7381 | 41.42 | 63.583 | 1105.8949
42 | 38490 | 5065.7291 | 38.49 | 68.6487 | 1292.1931
43 | 35710 | 4755.3379 | 35.71 | 73.4041 | 1483.0365
44 | 33130 | 4613.9862 | 33.13 | 78.018 | 1672.4189
45 | 30510 | 4597.8771 | 30.51 | 82.6159 | 1876.8262
46 | 27950 | 3606.9578 | 27.95 | 86.2229 | 2088.3229
47 | 26450 | 3261.4258 | 26.45 | 89.4843 | 2217.6572
48 | 24280 | 3847.9492 | 24.28 | 93.3322 | 2411.8382
49 | 22120 | 3847.9492 | 22.12 | 97.1802 | 2613.4358
50 | 19950 | 2479.3945 | 19.95 | 99.6596 | 2824.3168
51 | 19330 | 586.5234 | 19.33 | 100.2461 | 2886.1058 | Flange
52 | 19290 | 199 | 19.29 | 100.4451 | 2890.1156
53 | 19150 | 295 | 19.15 | 100.7401 | 2904.1779 | Flange
54 | 18975 | 199.9512 | 18.975 | 100.9401 | 2921.8075
55 | 18925 | 8985.0276 | 18.925 | 109.9251 | 2926.8545
56 | 7360 | 19090.5254 | 7.36 | 129.0156 | 4198.1382
57 | 5360 | 12696.0159 | 5.36 | 141.7116 | 4456.1694
58 | 540 | 43853.9945 | 0.54 | 185.5656 | 5139.2195
59 | -1460 | 15894 | -1.46 | 201.4596 | 5510.3507
60 | -5000 | 16000 | -5 | 217.4596 | 6223.5178
61 | -8000 | 164979.5715 | -8 | 382.4392 | 6875.8967
62 | -11345 | 70353.7618 | -11.345 | 452.793 | 8155.1558
63 | -15000 | 209333.3333 | -15 | 662.1263 | 9810.1141
64 | -24000 | 136788.6762 | -24 | 798.915 | 15769.2508
65 | -27300 | 321220.0957 | -27.3 | 1120.1351 | 18405.6702
66 | -30900 | 472690.1727 | -30.9 | 1592.8252 | 22438.1564
67 | -34000 | 472690.1727 | -34 | 2065.5154 | 27375.9147

## Geometry input sheet
Tower-Pile
Location: 'WD 34.6m / PD 28.75m'
| Elevation | [7 empty] | Yield
Nr | Top | Bottom | Height | Thickness | OD Top | OD Bottom | Mass | Material | Stress
| [mm] | [mm] | [mm LAT] | [mm] | [mm] | [mm] | [kg] |  | [MPa]
1 | 105810 | 105680 | 130 | 109.3 | 4605 | 4530 | 1562.2214 | S355 | 320
2
3
4
5 | 104720 | 104690 | 30 | 24 | 4529 | 4529 | 79.992 | S355 | 345
6 | 104690 | 104610 | 80 | 161 | 4529 | 4529 | 1387.4522 | S355 | 320 | Part 1
7 | 104610 | 104520 | 90 | 170.3 | 4529 | 4529 | 1647.5313 | S355 | 320 | Part 2
8 | 104520 | 104490 | 30 | 24 | 4529 | 4525 | 79.9565 | S355 | 345
9
10
11
12
13
14
15
16
17
18
19 | 77700 | 74970 | 2730 | 19.8 | 5352 | 5436 | 7164.0926 | S355 | 345
20 | 74970 | 72250 | 2720 | 20.4 | 5436 | 5521 | 7468.9592 | S355 | 345
21 | 72250 | 72220 | 30 | 21 | 5521 | 5521 | 85.4521 | S355 | 345
22 | 72220 | 72130 | 90 | 224.8 | 5521 | 5521 | 2642.547 | S355 | 320 | Part 2
23 | 72130 | 72040 | 90 | 224.8 | 5521 | 5521 | 2642.547 | S355 | 320 | Part 3
24 | 72040 | 72010 | 30 | 21 | 5521 | 5521 | 85.4521 | S355 | 345
25 | 72010 | 69410 | 2600 | 21 | 5521 | 5611 | 7466.4425 | S355 | 345
26
27
28
29
30
31
32
33
34
35 | 45990 | 43720 | 2270 | 25 | 6411 | 6489 | 8992.0462 | S355 | 345
36 | 43720 | 43680 | 40 | 26 | 6489 | 6489 | 165.7628 | S355 | 345
37 | 43680 | 43570 | 110 | 227.5 | 6489 | 6489 | 3864.3104 | S355 | 320 | Part 3
38 | 43570 | 43460 | 110 | 227.5 | 6489 | 6489 | 3864.3104 | S355 | 320 | Part 4
39 | 43460 | 43420 | 40 | 26 | 6489 | 6489 | 165.7628 | S355 | 345
40
41
42
43
44
45
46
47
48
49
50
51 | 19330 | 19290 | 40 | 37 | 6500 | 6500 | 235.8932 | S355 | 345
52 | 19290 | 19150 | 140 | 245 | 6500 | 6500 | 5291.039 | S355 | 320 | Tower
53 | 19150 | 18975 | 175 | 215 | 6500 | 6500 | 5831.7825 | S355 | 320 | Monopile
54 | 18975 | 18925 | 50 | 69 | 6500 | 6500 | 547.1635 | S355 | 325
55 | 18925 | 7360 | 11565 | 69 | 6500 | 6500 | 126558.922 | S355 | 325
56
57
58
59
60
61
62
63
64
65
66
67
68 | -45600 | -61350 | 15750 | 62 | 7400 | 7400 | 176713.4007 | S355 | 335
69 | -61350 | -63350 | 2000 | 77 | 7400 | 7400 | 27811.812 | S355 | 325
70 | -63350 | -63350 | 0 | 77 | 7400 | 7400 | 0 | S355 | 325

## Masses input sheet
Masses
Z-axis reference = | LAT
Positive direction Z-axis = | Upward
Location: 'WD 34.6m / PD 28.75m'
Nr. | Item | COG |  |  | Mass | Mass moment of inertia
|  | X [mm] | Y [mm] | Z [mm LAT] | [kg] | Ixx [kgm^2] | Iyy [kgm^2] | Izz [kgm^2]
1 | RNA & tower-top adapter mass | 0 | -781.1242 | 108045.2377 | 478384 | 52610684.7896 | 96182584.6531 | 52808100.1365
2 | Tower internals | 0 | 0 | 105580 | 3.6108 | 0 | 0 | 0
3 | Tower internals | 0 | 0 | 105480 | 27.4387 | 0 | 0 | 0
4 | Tower internals | 0 | 0 | 104490 | 61.0713 | 0 | 0 | 0
5 | Tower internals | 0 | 0 | 102390 | 65.3023 | 0 | 0 | 0
6 | Damper | 0 | 0 | 99630 | 25066.2647 | 0 | 0 | 0
1 | Tower internals | 0 | 0 | 22120 | 166.3637 | 0 | 0 | 0
2 | Tower internals | 0 | 0 | 19950 | 47.5325 | 0 | 0 | 0 | Tower
3 | Main Platform | 0 | 0 | 18500 | 15000 | 0 | 0 | 0 | Mono pile
4 | Hang-off platform | 0 | 0 | 17950 | 6500 | 0 | 0 | 0
5 | Upper ladder | 0 | 0 | 14000 | 3000 | 0 | 0 | 0
6 | Boatlanding + ladder | 0 | 0 | 4500 | 20000 | 0 | 0 | 0

## Loads input sheet
Loads
Location: 'WD 34.6m / PD 28.75m'
Section nr | Distance top of Section to LAT | Horizontal Force F
[-] | [mm LAT] | [N]
Hub height | 108900 | 525081.4023
1 | 105810 | 0
2 | 105680 | 142.8916
3 | 105580 | 123.8672
4 | 105480 | 532.5943
5 | 104720 | 489.202
6 | 104690 | 68.1119
7 | 104610 | 105.2639
8 | 104520 | 74.2984
9 | 104490 | 1323.5729
10 | 102390 | 3052.0355
11 | 99630 | 3518.7204
12 | 96880 | 3576.2891
63 | -15000 | 209333.3333
64 | -24000 | 136788.6762
65 | -27300 | 321220.0957
66 | -30900 | 472690.1727
67 | -34000 | 472690.1727
68 | -45600 | 0
69 | -61350 | 0
70 | -63350 | 0

## P-Y curves Wind farm2
PY-curves
Level [mLAT]
Number | 113 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90 | 91 | 92 | 93 | 94 | 95 | 96 | 97 | 98 | 99 | 100 | 101 | 102 | 103 | 104 | 105 | 106 | 107 | 108 | 109 | 110 | 111 | 112 | 113
| Number | Penetration depth [m]
Y [m] | 1 | 0 | 0 | 1.3102e-05 | 2.6204e-05 | 3.9305e-05 | 5.2407e-05 | 6.5509e-05 | 7.8611e-05 | 9.1713e-05 | 0.00010481 | 0.00011792 | 0.00013102 | 0.00014412 | 0.00015722 | 0.00017032 | 0.00018343 | 0.00019653 | 0.00020963 | 0.00022273 | 0.00023583 | 0.00024893 | 0.00026204 | 0.00027514 | 0.00028824 | 0.00030134 | 0.00031444 | 0.00032755 | 0.00034065 | 0.00035375 | 0.00036685 | 0.00037995 | 0.00039305 | 0.00047028 | 0.0005475 | 0.00062473 | 0.00070195 | 0.00077917 | 0.0008564 | 0.00093362 | 0.0010108 | 0.0010881 | 0.0011653 | 0.0012425 | 0.0013197 | 0.001397 | 0.0014742 | 0.0015514 | 0.0016286 | 0.0017059 | 0.0017831 | 0.0018603 | 0.0019375 | 0.0020148 | 0.002092 | 0.0021692 | 0.0022464 | 0.0023237 | 0.0026387 | 0.0029537 | 0.0032687 | 0.0035837 | 0.0038987 | 0.0042137 | 0.0045287 | 0.0048437 | 0.0051587 | 0.0054737 | 0.0057887 | 0.0061037 | 0.0064187 | 0.0067337 | 0.0070487 | 0.0073637 | 0.0076787 | 0.0079937 | 0.0083087 | 0.0086237 | 0.0097651 | 0.010907 | 0.012048 | 0.013189 | 0.014331 | 0.015472 | 0.016614 | 0.017755 | 0.018897 | 0.020038 | 0.02118 | 0.022321 | 0.023463 | 0.024604 | 0.025745 | 0.031723 | 0.037702 | 0.04368 | 0.049658 | 0.055636 | 0.061614 | 0.067592 | 0.07357 | 0.079548 | 0.085526 | 0.14639 | 0.20726 | 0.26812 | 0.32899 | 0.38985 | 0.89038 | 1.3909 | 1.8914 | 2.3919 | 2.8925 | 15
The soil resistance p as a force per unit depth in [N/m].
| 2 | -34.6 | 0 | 1452.7935 | 2739.5126 | 3983.0611 | 4991.3318 | 5999.6025 | 7007.8732 | 7920.449 | 8662.6721 | 9404.8952 | 10147.1183 | 10889.3413 | 11631.5644 | 12373.7875 | 13116.0106 | 13858.2336 | 14600.4567 | 15331.7189 | 15846.2101 | 16360.7013 | 16875.1925 | 17389.6838 | 17904.175 | 18418.6662 | 18933.1574 | 19447.6487 | 19962.1399 | 20476.6311 | 20991.1223 | 21505.6136 | 22020.1048 | 24406.3983 | 26502.2565 | 28598.1147 | 30667.5516 | 32071.7625 | 33475.9733 | 34880.1841 | 36284.395 | 37688.6058 | 38792.1174 | 39684.7804 | 40577.4435 | 41470.1065 | 42362.7695 | 43255.4326 | 44148.0956 | 45040.7587 | 45924.7543 | 46201.0925 | 46477.4307 | 46753.7689 | 47030.107 | 47306.4452 | 47582.7834 | 47859.1216 | 48986.3168 | 50113.512 | 51240.7073 | 52367.9025 | 53495.0977 | 54622.293 | 55749.4882 | 56876.6834 | 58003.8787 | 59131.0739 | 60258.2691 | 61385.4644 | 62512.6596 | 63639.8548 | 64767.0501 | 65222.0195 | 65446.8176 | 65671.6156 | 65896.4137 | 66121.2117 | 66935.8013 | 67750.3908 | 68564.9804 | 69379.57 | 70194.1596 | 71008.7491 | 71823.3387 | 72637.9283 | 72889.1026 | 73087.2162 | 73285.3297 | 73483.4432 | 73681.5567 | 73879.6703 | 74077.7838 | 75115.3523 | 75813.9598 | 75934.433 | 76054.9063 | 76175.3795 | 76295.8528 | 76416.326 | 76527.1302 | 76527.133 | 76527.1357 | 76527.1638 | 76527.1919 | 76527.22 | 76527.248 | 76527.2761 | 76527.507 | 76527.7378 | 76527.9687 | 76528.1996 | 76528.4304 | 76534.015
| 3 | -35.1 | 0 | 3269.9952 | 6075.4387 | 8880.8822 | 11470.4952 | 13657.049 | 15843.6028 | 18030.1567 | 20216.7105 | 22148.2869 | 23770.177 | 25392.0672 | 27013.9573 | 28635.8474 | 30257.7376 | 31879.6277 | 33501.5178 | 35123.408 | 36745.2981 | 38367.1882 | 39989.0783 | 41610.9685 | 43109.34 | 44231.688 | 45354.036 | 46476.384 | 47598.732 | 48721.0801 | 49843.4281 | 50965.7761 | 52088.1241 | 58703.4139 | 64987.3548 | 69555.9252 | 74124.4956 | 78693.066 | 83261.6364 | 87115.2389 | 90176.1721 | 93237.1053 | 96298.0386 | 99358.9718 | 102419.9051 | 105480.8383 | 108009.3388 | 109955.6993 | 111902.0598 | 113848.4202 | 115794.7807 | 117741.1412 | 119687.5017 | 121633.8621 | 123580.2226 | 125526.5831 | 127472.9436 | 128781.4613 | 131239.2062 | 133696.951 | 136154.6959 | 138612.4408 | 141070.1857 | 143527.9306 | 145985.6754 | 148443.4203 | 150901.1652 | 153358.9101 | 155816.655 | 158274.3999 | 160732.1447 | 163189.8896 | 165647.6345 | 168105.3794 | 170563.1243 | 173020.8691 | 175478.614 | 177936.3589 | 182993.8891 | 184769.8578 | 186545.8266 | 188321.7954 | 190097.7642 | 191873.733 | 193649.7018 | 195425.6706 | 197201.6394 | 198977.6082 | 200753.577 | 202529.5457 | 203658.9672 | 204090.9258 | 204522.8843 | 206785.1558 | 209047.4273 | 211309.6988 | 212198.006 | 212460.6622 | 212723.3184 | 212985.9746 | 213248.6308 | 213511.287 | 213773.9433 | 214137.768 | 214137.8467 | 214137.9255 | 214138.0042 | 214138.0829 | 214138.7303 | 214139.3777 | 214140.0251 | 214140.6725 | 214141.3199 | 214156.98
| 54 | -60.6 | 0 | 9293.8334 | 18587.6669 | 27881.5003 | 37175.3337 | 46469.1671 | 55763.0006 | 65056.834 | 74350.6674 | 83644.5009 | 92938.3343 | 102232.1677 | 111526.0011 | 120819.8346 | 130113.668 | 139295.6192 | 146573.1403 | 153850.6614 | 161128.1825 | 168405.7036 | 175683.2248 | 182960.7459 | 190238.267 | 197515.7881 | 204793.3093 | 212070.8304 | 219348.3515 | 226625.8726 | 233903.3937 | 241180.9149 | 248458.436 | 291353.2513 | 334248.0666 | 377142.8819 | 420037.6972 | 462932.5125 | 505827.3278 | 548722.1431 | 591616.9584 | 634511.7737 | 677406.589 | 714715.5611 | 748338.5778 | 781961.5945 | 815584.6112 | 849207.628 | 882830.6447 | 916453.6614 | 950076.6781 | 983699.6948 | 1017322.7115 | 1050945.7283 | 1084568.745 | 1118191.7617 | 1151814.7784 | 1185437.7951 | 1322587.5189 | 1441042.9261 | 1541988.7465 | 1642934.5669 | 1743880.3873 | 1844826.2078 | 1945772.0282 | 2046717.8486 | 2147663.669 | 2248609.4894 | 2349555.3098 | 2450501.1302 | 2551446.9506 | 2652392.7711 | 2753338.5915 | 2830859.1564 | 2900872.9637 | 2970886.771 | 3040900.5783 | 3110914.3855 | 3364619.9738 | 3618325.5621 | 3872031.1504 | 4125736.7386 | 4313596.4092 | 4488757.2084 | 4663918.0077 | 4839078.8069 | 5014239.6062 | 5189400.4054 | 5364561.2047 | 5539722.004 | 5662335.3842 | 5779684.1158 | 5897032.8475 | 6511616.5656 | 7060117.2606 | 7451068.5293 | 7842019.7979 | 8232971.0665 | 8423383.7262 | 8544371.0811 | 8665358.436 | 8786345.7908 | 8907333.1457 | 10139157.4789 | 11370981.812 | 11964753.0985 | 12210417.9266 | 12456082.7548 | 13506423.6476 | 13779025.6441 | 13836074.1989 | 13887799.6172 | 13887849.0573 | 13889045
| 55 | -61.1 | 0 | 6381.9322 | 12763.8643 | 19145.7965 | 25527.7287 | 31909.6608 | 38291.593 | 44673.5251 | 51055.4573 | 57437.3895 | 63819.3216 | 70201.2538 | 76583.186 | 82965.1181 | 89347.0503 | 95728.9824 | 101009.3402 | 106007.354 | 111005.3678 | 116003.3817 | 121001.3955 | 125999.4093 | 130997.4231 | 135995.4369 | 140993.4507 | 145991.4646 | 150989.4784 | 155987.4922 | 160985.506 | 165983.5198 | 170981.5337 | 200440.5866 | 229899.6395 | 259358.6923 | 288817.7452 | 318276.7981 | 347735.851 | 377194.9039 | 406653.9568 | 436113.0097 | 465572.0626 | 492896.9659 | 515990.0884 | 539083.2109 | 562176.3334 | 585269.456 | 608362.5785 | 631455.701 | 654548.8235 | 677641.9461 | 700735.0686 | 723828.1911 | 746921.3136 | 770014.4362 | 793107.5587 | 816200.6812 | 910398.516 | 995542.599 | 1064866.1877 | 1134189.7764 | 1203513.3651 | 1272836.9538 | 1342160.5425 | 1411484.1312 | 1480807.7199 | 1550131.3086 | 1619454.8973 | 1688778.486 | 1758102.0746 | 1827425.6633 | 1896749.252 | 1958273.3194 | 2006353.8104 | 2054434.3015 | 2102514.7925 | 2150595.2835 | 2324822.193 | 2499049.1025 | 2673276.012 | 2847502.9215 | 2987432.2297 | 3107727.7694 | 3228023.3091 | 3348318.8489 | 3468614.3886 | 3588909.9284 | 3709205.4681 | 3829501.0078 | 3927169.1337 | 4007759.9804 | 4088350.8272 | 4510424.6031 | 4903044.1461 | 5171538.9752 | 5440033.8043 | 5708528.6333 | 5869877.6632 | 5952966.4647 | 6036055.2662 | 6119144.0677 | 6202232.8693 | 7048195.7189 | 7894158.5686 | 8345853.9488 | 8514567.0371 | 8683280.1255 | 9425345.7098 | 9624265.6456 | 9663444.1772 | 9702131.4349 | 9702166.0865 | 9703004.3
| 56 | -61.6 | 0 | 6409.5321 | 12819.0642 | 19228.5963 | 25638.1284 | 32047.6604 | 38457.1925 | 44866.7246 | 51276.2567 | 57685.7888 | 64095.3209 | 70504.853 | 76914.3851 | 83323.9172 | 89733.4492 | 96142.9813 | 102082.178 | 107100.3084 | 112118.4388 | 117136.5691 | 122154.6995 | 127172.8298 | 132190.9602 | 137209.0905 | 142227.2209 | 147245.3512 | 152263.4816 | 157281.6119 | 162299.7423 | 167317.8727 | 172336.003 | 201913.6258 | 231491.2486 | 261068.8714 | 290646.4943 | 320224.1171 | 349801.7399 | 379379.3627 | 408956.9855 | 438534.6083 | 468112.2311 | 497689.8539 | 521795.91 | 544986.4681 | 568177.0261 | 591367.5842 | 614558.1423 | 637748.7004 | 660939.2584 | 684129.8165 | 707320.3746 | 730510.9326 | 753701.4907 | 776892.0488 | 800082.6068 | 823273.1649 | 917868.4435 | 1010190.201 | 1079792.1416 | 1149394.0821 | 1218996.0226 | 1288597.9631 | 1358199.9036 | 1427801.8442 | 1497403.7847 | 1567005.7252 | 1636607.6657 | 1706209.6063 | 1775811.5468 | 1845413.4873 | 1915015.4278 | 1984617.3683 | 2039973.0534 | 2088251.7096 | 2136530.3658 | 2184809.022 | 2359754.0129 | 2534699.0038 | 2709643.9948 | 2884588.9857 | 3044686.2224 | 3165467.7351 | 3286249.2477 | 3407030.7604 | 3527812.273 | 3648593.7857 | 3769375.2984 | 3890156.811 | 4010938.3237 | 4093342.0643 | 4174261.7557 | 4598057.7705 | 5020922.4376 | 5290507.187 | 5560091.9364 | 5829676.6858 | 6046706.1572 | 6130133.8082 | 6213561.4592 | 6296989.1102 | 6380416.7612 | 7229829.5831 | 8079242.405 | 8611746.3025 | 8781146.621 | 8950546.9396 | 9732920.9271 | 9953706.4582 | 9993044.7609 | 10032383.0636 | 10037616.2717 | 10038488
| 57 | -62.1 | 0 | 6432.8908 | 12865.7817 | 19298.6725 | 25731.5633 | 32164.4542 | 38597.345 | 45030.2358 | 51463.1267 | 57896.0175 | 64328.9084 | 70761.7992 | 77194.69 | 83627.5809 | 90060.4717 | 96493.3625 | 102926.2534 | 108153.2694 | 113191.7831 | 118230.2967 | 123268.8104 | 128307.324 | 133345.8376 | 138384.3513 | 143422.8649 | 148461.3786 | 153499.8922 | 158538.4059 | 163576.9195 | 168615.4332 | 173653.9468 | 203351.7118 | 233049.4768 | 262747.2419 | 292445.0069 | 322142.7719 | 351840.5369 | 381538.3019 | 411236.0669 | 440933.832 | 470631.597 | 500329.362 | 527642.4955 | 550930.1108 | 574217.7261 | 597505.3413 | 620792.9566 | 644080.5719 | 667368.1872 | 690655.8024 | 713943.4177 | 737231.033 | 760518.6483 | 783806.2635 | 807093.8788 | 830381.4941 | 925372.6731 | 1020363.8522 | 1094890.6374 | 1164765.1845 | 1234639.7316 | 1304514.2786 | 1374388.8257 | 1444263.3728 | 1514137.9199 | 1584012.467 | 1653887.0141 | 1723761.5612 | 1793636.1083 | 1863510.6553 | 1933385.2024 | 2003259.7495 | 2073134.2966 | 2122455.1054 | 2170923.3311 | 2219391.5567 | 2395023.481 | 2570655.4053 | 2746287.3296 | 2921919.2539 | 3097551.1781 | 3223871.2978 | 3345138.2808 | 3466405.2637 | 3587672.2467 | 3708939.2297 | 3830206.2127 | 3951473.1957 | 4072740.1787 | 4180088.5596 | 4261332.2946 | 4686825.4042 | 5112318.5138 | 5411173.9874 | 5681837.8181 | 5952501.6488 | 6223165.4795 | 6310092.858 | 6393853.2214 | 6477613.5849 | 6561373.9484 | 7414174.2595 | 8266974.5706 | 8881905.1054 | 9051982.2037 | 9222059.302 | 10045468.859 | 10288543.9358 | 10328039.0745 | 10367534.2132 | 10378575.067 | 10379483
| 58 | -62.6 | 0 | 6458.2301 | 12916.4601 | 19374.6902 | 25832.9202 | 32291.1503 | 38749.3803 | 45207.6104 | 51665.8404 | 58124.0705 | 64582.3005 | 71040.5306 | 77498.7606 | 83956.9907 | 90415.2207 | 96873.4508 | 103331.6809 | 109241.6724 | 114299.8884 | 119358.1044 | 124416.3204 | 129474.5365 | 134532.7525 | 139590.9685 | 144649.1846 | 149707.4006 | 154765.6166 | 159823.8327 | 164882.0487 | 169940.2647 | 174998.4808 | 204812.3747 | 234626.2685 | 264440.1624 | 294254.0563 | 324067.9502 | 353881.8441 | 383695.738 | 413509.6318 | 443323.5257 | 473137.4196 | 502951.3135 | 532765.2074 | 556901.1465 | 580272.1936 | 603643.2407 | 627014.2878 | 650385.3349 | 673756.382 | 697127.4291 | 720498.4762 | 743869.5233 | 767240.5704 | 790611.6175 | 813982.6646 | 837353.7117 | 932685.2128 | 1028016.7138 | 1109949.7843 | 1180107.3817 | 1250264.9791 | 1320422.5765 | 1390580.1739 | 1460737.7712 | 1530895.3686 | 1601052.966 | 1671210.5634 | 1741368.1608 | 1811525.7582 | 1881683.3556 | 1951840.953 | 2021998.5504 | 2092156.1478 | 2157076.2934 | 2205739.2807 | 2254402.268 | 2430739.9406 | 2607077.6132 | 2783415.2857 | 2959752.9583 | 3136090.6308 | 3283137.7983 | 3404876.9101 | 3526616.0219 | 3648355.1337 | 3770094.2455 | 3891833.3572 | 4013572.469 | 4135311.5808 | 4257050.6926 | 4349629.1478 | 4776772.9583 | 5203916.7688 | 5533545.2686 | 5805274.9088 | 6077004.549 | 6348734.1892 | 6492846.4554 | 6576934.8751 | 6661023.2948 | 6745111.7145 | 7601252.1069 | 8457392.4993 | 9156339.2187 | 9327081.7454 | 9497824.2721 | 10362991.1058 | 10628778.668 | 10668428.5615 | 10708078.4549 | 10725044.3172 | 10725987
| 59 | -63.1 | 0 | 6485.3969 | 12970.7937 | 19456.1906 | 25941.5874 | 32426.9843 | 38912.3811 | 45397.778 | 51883.1748 | 58368.5717 | 64853.9685 | 71339.3654 | 77824.7623 | 84310.1591 | 90795.556 | 97280.9528 | 103766.3497 | 110251.7465 | 115443.9541 | 120521.2273 | 125598.5005 | 130675.7737 | 135753.0469 | 140830.3201 | 145907.5933 | 150984.8664 | 156062.1396 | 161139.4128 | 166216.686 | 171293.9592 | 176371.2324 | 206297.4521 | 236223.6717 | 266149.8914 | 296076.1111 | 326002.3307 | 355928.5504 | 385854.7701 | 415780.9897 | 445707.2094 | 475633.4291 | 505559.6488 | 535485.8684 | 562928.7602 | 586396.2531 | 609863.7461 | 633331.239 | 656798.7319 | 680266.2249 | 703733.7178 | 727201.2107 | 750668.7037 | 774136.1966 | 797603.6896 | 821071.1825 | 844538.6754 | 940263.5832 | 1035988.4909 | 1125394.5948 | 1195813.4379 | 1266232.2809 | 1336651.124 | 1407069.9671 | 1477488.8101 | 1547907.6532 | 1618326.4963 | 1688745.3393 | 1759164.1824 | 1829583.0255 | 1900001.8685 | 1970420.7116 | 2040839.5547 | 2111258.3977 | 2181677.2408 | 2240924.5619 | 2289774.6453 | 2466790.2886 | 2643805.932 | 2820821.5754 | 2997837.2187 | 3174852.8621 | 3343063.1007 | 3465261.673 | 3587460.2453 | 3709658.8175 | 3831857.3898 | 3954055.9621 | 4076254.5344 | 4198453.1067 | 4320651.679 | 4439020.7632 | 4867823.2167 | 5296625.6703 | 5657612.2786 | 5930384.3696 | 6203156.4606 | 6475928.5517 | 6678380.7917 | 6762791.8064 | 6847202.8212 | 6931613.836 | 7791038.7078 | 8650463.5795 | 9435041.5687 | 9606440.0638 | 9777838.5589 | 10685488.8881 | 10974410.7161 | 11014212.9928 | 11054015.2695 | 11077023.1098 | 11078003
| 60 | -63.6 | 0 | 6508.5781 | 13017.1562 | 19525.7343 | 26034.3125 | 32542.8906 | 39051.4687 | 45560.0468 | 52068.6249 | 58577.203 | 65085.7811 | 71594.3592 | 78102.9374 | 84611.5155 | 91120.0936 | 97628.6717 | 104137.2498 | 110645.8279 | 116547.4009 | 121643.9948 | 126740.5886 | 131837.1825 | 136933.7764 | 142030.3703 | 147126.9642 | 152223.5581 | 157320.1519 | 162416.7458 | 167513.3397 | 172609.9336 | 177706.5275 | 207746.6262 | 237786.725 | 267826.8238 | 297866.9225 | 327907.0213 | 357947.1201 | 387987.2188 | 418027.3176 | 448067.4163 | 478107.5151 | 508147.6139 | 538187.7126 | 568227.8114 | 592546.4052 | 616097.1962 | 639647.9872 | 663198.7782 | 686749.5692 | 710300.3602 | 733851.1512 | 757401.9422 | 780952.7331 | 804503.5241 | 828054.3151 | 851605.1061 | 947669.7902 | 1043734.4743 | 1139799.1583 | 1211483.8088 | 1282173.9378 | 1352864.0669 | 1423554.1959 | 1494244.3249 | 1564934.454 | 1635624.583 | 1706314.7121 | 1777004.8411 | 1847694.9701 | 1918385.0992 | 1989075.2282 | 2059765.3572 | 2130455.4863 | 2201145.6153 | 2271835.7443 | 2325550.5035 | 2503212.9347 | 2680875.3659 | 2858537.797 | 3036200.2282 | 3213862.6594 | 3391525.0906 | 3526318.0699 | 3648987.1139 | 3771656.158 | 3894325.2021 | 4016994.2461 | 4139663.2902 | 4262332.3343 | 4385001.3783 | 4507670.4224 | 4960064.2036 | 5390482.1475 | 5783392.6051 | 6057193.3579 | 6330994.1107 | 6604794.8635 | 6866711.4022 | 6951440.5118 | 7036169.6215 | 7120898.7311 | 7983562.2638 | 8846225.7965 | 9708889.3292 | 9890065.1541 | 10062109.1807 | 11012963.502 | 11325440.3105 | 11365392.2919 | 11405344.2732 | 11434510.3693 | 11435528

## Verification Resonance Tower
Resonance frequency tower
Tower geometry
Hub Height at | 108.045 | [m LAT]
Top tower at | 105.81 | [mLAT]
Bottom tower at | 19.15 | [m LAT]
| Excel Input | FEM | Difference |  | Status
Tower wall height | 86660 | 86660 | 0 | [mm] | Oke
Tower - Nacelle | 2235.2377 | 2235.238 | 0.00032483 | [mm] | Oke
Tower shell mass |  |  |  | [kg] | Oke
Tower added mass |  |  |  | [kg] | Oke
Resonance Frequencies
1st resonance mode |  | 0.3084 | Hz | 1st bending side-side
|  | 0.3136 | Hz | 1st bending fore-aft
2e resonance mode |  |  | Hz | 1st torsion
3rd resonance mode |  |  | Hz | 2nd bending side-side
|  |  | Hz | 2nd bending fore-aft
FE-model
1st resonance mode
1st bending side-side | [5 empty] | 1st bending fore-aft
2e resonance mode
1st torsion
3rd resonance mode
2nd bending side-side | [5 empty] | 2nd bending fore-aft

## Verification Resonance Foundati
Resonance frequency total foundation
Tower geometry
Hub Height at | 108.045 | [m LAT]
Top tower at | 105.81 | [mLAT]
Bottom tower at | 19.15 | [m LAT]
Top pile at | 19.15 | [m LAT]
Bottom pile at | -63.35 | [m LAT]
| Excel Input | FEM | Difference |  | Status
Tower wall height | 86660 | 86660 | 0 | [mm] | Oke
Tower - Nacelle | 2235.2377 | 2235.238 | 0.00032483 | [mm] | Oke
Tower shell mass |  |  |  | [kg] | Oke
Tower added mass |  |  |  | [kg] | Oke
Pile length |  |  |  | [mm] | Oke
Pile shell mass |  |  |  | [kg] | Oke
Pile added mass |  |  |  | [kg] | Oke
Mass internal water in pile |  |  |  | [kg]
Added external water mass |  | 1801470 |  | [kg]
Resonance Frequencies
1st resonance mode |  | 0.205 | Hz | 1st bending side-side
|  |  | Hz | 1st bending fore-aft
2e resonance mode |  |  | Hz | 2nd bending side-side
|  |  | Hz | 2nd bending fore-aft
3rd resonance mode |  |  | Hz | 1st torsion
4th resonance mode |  |  | Hz | 3rd bending side-side
|  | 1.7883 | Hz | 3rd bending fore-aft
FE-model
1st resonance mode
1st bending side-side | [5 empty] | 1st bending fore-aft
2nd resonance mode
2nd bending side-side | [5 empty] | 2nd bending fore-aft
3rd resonance mode
1st torsion
4th resonance mode
3rd bending side-side | [5 empty] | 3rd bending fore-aft

## Verification foundation load
Turbine, wind, wave and current load
Tower geometry
Hub Height at | 108.045 | [m LAT]
Top tower at | 105.81 | [mLAT]
Bottom tower at | 19.15 | [m LAT]
Top pile at | 19.15 | [m LAT]
Bottom pile at | -63.35 | [m LAT]
Applied load according to sheet 'Loads input sheet', including gravity load of 9.81 [m/s^2].
Calculation executed with 'Large displacement on', so the excentricity caused by the bending of the foundation leads to an additional bending moment
due to the gravity load.
The maximum lateral displacement is equal to 0.718 [m]
The applied load (theoretical Shear load) and the theoretical calculated Bending load, see sheet 'Wind farm 2 Loads')
are compared with the Shear load and Bending moment following from FEM.
The graphs below show:
1. The Theoretical applied shear load corresponds with the shear load following from FEM.
2. The resulting theoretical bending moment corresponds well with the bending load following From FEM.
The difference near the top of the foundation is caused by the gravity load acting on the tower and the turbine.
The excentric position of the COG of the turbine relative to the centre line of the foundation leads to a negative moment due to the effect of the gravity
3. The bending moment in the foundation reaches its maximum value inside the soil, at LAT-40m.
Lower down the bending moment reduces to 0 and the shear force becomes negative.
Z | FY | FZ | MX
[m LAT] | [kN] | [kN] | [kNm]
105.81 | 525.08 | 4692.9 | -2403.3
105.68 | 525.22 | 4708.9 | -2330.1
105.58 | 525.35 | 4711.7 | -2273.8
105.48 | 525.88 | 4714.7 | -2217.4
105.1 | 525.88 | 4725 | -2002.9
104.72 | 526.37 | 4735.4 | -1788.3
104.69 | 526.44 | 4736.1 | -1771.4
104.61 | 526.54 | 4749.8 | -1726.2
104.52 | 526.62 | 4765.9 | -1675.3
104.49 | 527.94 | 4767.3 | -1658.3
103.965 | 527.94 | 4778.8 | -1360.6
103.44 | 527.94 | 4790.3 | -1062.8
102.915 | 527.94 | 4801.8 | -764.97
102.39 | 530.99 | 4814 | -467.08
101.93 | 530.99 | 4822.2 | -204.6
101.47 | 530.99 | 4830.4 | 57.91
101.01 | 530.99 | 4838.6 | 320.45
100.55 | 530.99 | 4846.8 | 583.02
100.09 | 530.99 | 4855 | 845.62
99.63 | 534.51 | 5109.2 | 1108.2
99.1717 | 534.51 | 5117.5 | 1372.5
98.7133 | 534.51 | 5125.8 | 1636.7
98.255 | 534.51 | 5134.1 | 1901
97.7967 | 534.51 | 5142.5 | 2165.3
97.3383 | 534.51 | 5150.8 | 2429.6
96.88 | 538.09 | 5159.9 | 2693.9
96.4217 | 538.09 | 5168.3 | 2959.8
95.9633 | 538.09 | 5176.8 | 3225.8
95.505 | 538.09 | 5185.2 | 3491.8
95.0467 | 538.09 | 5193.7 | 3757.8
94.5883 | 538.09 | 5202.3 | 4023.8
94.13 | 541.73 | 5211.5 | 4289.8
93.6717 | 541.73 | 5220.3 | 4557.4
93.2133 | 541.73 | 5229.1 | 4825.1
92.755 | 541.73 | 5237.9 | 5092.7
92.2967 | 541.73 | 5246.8 | 5360.4
91.8383 | 541.73 | 5255.7 | 5628
91.38 | 545.43 | 5265.3 | 5895.7
90.9233 | 545.43 | 5274.4 | 6164
90.4667 | 545.43 | 5283.5 | 6432.4
90.01 | 545.43 | 5292.6 | 6700.7
89.5533 | 545.43 | 5301.8 | 6969
89.0967 | 545.43 | 5310.9 | 7237.3
88.64 | 549.18 | 5320.9 | 7505.6
88.1833 | 549.18 | 5330.3 | 7775.6
87.7267 | 549.18 | 5339.8 | 8045.6
87.27 | 549.18 | 5349.3 | 8315.6
86.8133 | 549.18 | 5358.8 | 8585.5
86.3567 | 549.18 | 5368.4 | 8855.4
85.9 | 553 | 5378.8 | 9125.3
85.4433 | 553 | 5388.8 | 9397
84.9867 | 553 | 5398.8 | 9668.6
84.53 | 553 | 5408.9 | 9940.2
84.0733 | 553 | 5419 | 10212
83.6167 | 553 | 5429.1 | 10483
83.16 | 556.87 | 5440 | 10755
82.705 | 556.87 | 5450.6 | 11027
82.25 | 556.87 | 5461.1 | 11299
81.795 | 556.87 | 5471.7 | 11572
81.34 | 556.87 | 5482.3 | 11844
80.885 | 556.87 | 5493 | 12116
80.43 | 560.81 | 5504.5 | 12388
79.975 | 560.81 | 5515.6 | 12662
79.52 | 560.81 | 5526.7 | 12936
79.065 | 560.81 | 5537.8 | 13210
78.61 | 560.81 | 5548.9 | 13484
78.155 | 560.81 | 5560.1 | 13757
77.7 | 564.8 | 5572.2 | 14031
77.245 | 564.8 | 5583.8 | 14307
76.79 | 564.8 | 5595.5 | 14582
76.335 | 564.8 | 5607.2 | 14858
75.88 | 564.8 | 5618.9 | 15133
75.425 | 564.8 | 5630.7 | 15409
74.97 | 568.85 | 5643.4 | 15684
74.5167 | 568.85 | 5655.6 | 15960
74.0633 | 568.85 | 5667.7 | 16237
73.61 | 568.85 | 5679.9 | 16513
73.1567 | 568.85 | 5692.1 | 16789
72.7033 | 568.85 | 5704.4 | 17065
72.25 | 570.92 | 5716.7 | 17341
72.22 | 571.01 | 5717.5 | 17359
72.13 | 571.14 | 5743.5 | 17414
72.04 | 571.23 | 5769.4 | 17469
72.01 | 573.23 | 5771.2 | 17488
71.5767 | 573.23 | 5783.3 | 17754
71.1433 | 573.23 | 5795.5 | 18019
70.71 | 573.23 | 5807.7 | 18285
70.2767 | 573.23 | 5819.9 | 18551
69.8433 | 573.23 | 5832.1 | 18817
69.41 | 577.3 | 5845.5 | 19083
68.96 | 577.3 | 5858.6 | 19360
68.51 | 577.3 | 5871.7 | 19638
68.06 | 577.3 | 5884.9 | 19916
67.61 | 577.3 | 5898.1 | 20193
67.16 | 577.3 | 5911.3 | 20471
66.71 | 581.5 | 5925.7 | 20749
66.2617 | 581.5 | 5939.3 | 21027
65.8133 | 581.5 | 5952.9 | 21305
65.365 | 581.5 | 5966.5 | 21584
64.9167 | 581.5 | 5980.2 | 21862
64.4683 | 581.5 | 5993.9 | 22140
64.02 | 585.75 | 6008.8 | 22419
63.5733 | 585.75 | 6022.8 | 22698
63.1267 | 585.75 | 6036.9 | 22977
62.68 | 585.75 | 6051.1 | 23256
62.2333 | 585.75 | 6065.2 | 23535
61.7867 | 585.75 | 6079.4 | 23814
61.34 | 590.07 | 6094.8 | 24092
60.8917 | 590.07 | 6109.4 | 24374
60.4433 | 590.07 | 6124 | 24656
59.995 | 590.07 | 6138.7 | 24938
59.5467 | 590.07 | 6153.4 | 25220
59.0983 | 590.07 | 6168.1 | 25501
58.65 | 594.46 | 6184.1 | 25783
58.2033 | 594.46 | 6199.1 | 26065
57.7567 | 594.46 | 6214.1 | 26348
57.31 | 594.46 | 6229.2 | 26630
56.8633 | 594.46 | 6244.4 | 26913
56.4167 | 594.46 | 6259.5 | 27195
55.97 | 598.9 | 6275.9 | 27477
55.525 | 598.9 | 6291.4 | 27761
55.08 | 598.9 | 6306.9 | 28044
54.635 | 598.9 | 6322.4 | 28327
54.19 | 598.9 | 6338 | 28610
53.745 | 598.9 | 6353.6 | 28893
53.3 | 603.41 | 6370.5 | 29176
52.8533 | 603.41 | 6386.5 | 29462
52.4067 | 603.41 | 6402.5 | 29748
51.96 | 603.41 | 6418.6 | 30034
51.5133 | 603.41 | 6434.7 | 30320
51.0667 | 603.41 | 6450.9 | 30606
50.62 | 607.69 | 6468.2 | 30892
50.154 | 607.69 | 6485.4 | 31192
49.688 | 607.69 | 6502.6 | 31492
49.222 | 607.69 | 6519.8 | 31792
48.756 | 607.69 | 6537.1 | 32092
48.29 | 611.7 | 6555.6 | 32392
47.83 | 611.7 | 6572.9 | 32690
47.37 | 611.7 | 6590.3 | 32988
46.91 | 611.7 | 6607.8 | 33286
46.45 | 611.7 | 6625.3 | 33583
45.99 | 615.7 | 6644 | 33881
45.536 | 615.7 | 6661.5 | 34177
45.082 | 615.7 | 6679.1 | 34472
44.628 | 615.7 | 6696.8 | 34768
44.174 | 615.7 | 6714.5 | 35063
43.72 | 617.74 | 6732.2 | 35359
43.68 | 617.88 | 6733.8 | 35385
43.57 | 618.07 | 6771.7 | 35457
43.46 | 618.21 | 6809.6 | 35529
43.42 | 620.02 | 6812.3 | 35555
42.92 | 620.02 | 6832.7 | 35883
42.42 | 620.02 | 6853 | 36210
41.92 | 620.02 | 6873.3 | 36538
41.42 | 624.39 | 6895.2 | 36865
40.9317 | 624.39 | 6915 | 37187
40.4433 | 624.39 | 6934.9 | 37509
39.955 | 624.39 | 6954.7 | 37831
39.4667 | 624.39 | 6974.6 | 38153
38.9783 | 624.39 | 6994.4 | 38475
38.49 | 629.45 | 7015.8 | 38796
38.0267 | 629.45 | 7034.6 | 39104
37.5633 | 629.45 | 7053.4 | 39411
37.1 | 629.45 | 7072.3 | 39719
36.6367 | 629.45 | 7091.1 | 40026
36.1733 | 629.45 | 7109.9 | 40333
35.71 | 634.21 | 7130.1 | 40640
35.194 | 634.21 | 7151.1 | 40985
34.678 | 634.21 | 7172.1 | 41329
34.162 | 634.21 | 7193.1 | 41674
33.646 | 634.21 | 7214.1 | 42018
33.13 | 638.82 | 7776 | 42362
32.6933 | 638.82 | 7794.1 | 42656
32.2567 | 638.82 | 7812.2 | 42951
31.82 | 638.82 | 7830.3 | 43245
31.3833 | 638.82 | 7848.4 | 43539
30.9467 | 638.82 | 7866.5 | 43833
30.51 | 643.42 | 7886 | 44126
29.998 | 643.42 | 7908.5 | 44473
29.486 | 643.42 | 7930.9 | 44820
28.974 | 643.42 | 7953.3 | 45167
28.462 | 643.42 | 7975.7 | 45513
27.95 | 647.03 | 7999.3 | 45860
27.45 | 647.03 | 8028.2 | 46200
26.95 | 647.03 | 8057.2 | 46540
26.45 | 650.29 | 8087.7 | 46879
26.016 | 650.29 | 8112.8 | 47176
25.582 | 650.29 | 8137.9 | 47472
25.148 | 650.29 | 8163.1 | 47768
24.714 | 650.29 | 8188.2 | 48065
24.28 | 654.14 | 8214.9 | 48361
23.848 | 654.14 | 8239.9 | 48657
23.416 | 654.14 | 8264.9 | 48954
22.984 | 654.14 | 8289.9 | 49250
22.552 | 654.14 | 8314.9 | 49547
22.12 | 657.99 | 8341.5 | 49843
21.686 | 657.99 | 8366.6 | 50142
21.252 | 657.99 | 8391.7 | 50441
20.818 | 657.99 | 8416.8 | 50740
20.384 | 657.99 | 8441.9 | 51040
19.95 | 660.47 | 8467.5 | 51339
19.64 | 660.47 | 8485.4 | 51553
19.33 | 661.05 | 8503.4 | 51767
19.29 | 661.25 | 8505.7 | 51795
19.15 | 661.55 | 8557.6 | 51892
18.975 | 661.75 | 8614.8 | 52013
18.925 | 670.73 | 8620.2 | 52048
18.5 | 670.73 | 8812.9 | 52346
17.95 | 670.73 | 8935.7 | 52732
17.4563 | 670.73 | 8988.8 | 53079
16.9625 | 670.73 | 9041.8 | 53426
16.4688 | 670.73 | 9094.8 | 53773
15.975 | 670.73 | 9147.8 | 54120
15.4812 | 670.73 | 9200.8 | 54467
14.9875 | 670.73 | 9253.8 | 54814
14.4938 | 670.73 | 9306.8 | 55161
14 | 670.73 | 9389.2 | 55508
13.5257 | 670.73 | 9440.1 | 55841
13.0514 | 670.73 | 9491.1 | 56175
12.5771 | 670.73 | 9542 | 56508
12.1029 | 670.73 | 9592.9 | 56842
11.6286 | 670.73 | 9643.8 | 57175
11.1543 | 670.73 | 9694.7 | 57508
10.68 | 670.73 | 9745.6 | 57842
10.2057 | 670.73 | 9796.6 | 58175
9.7314 | 670.73 | 9847.5 | 58509
9.2571 | 670.73 | 9898.4 | 58842
8.7829 | 670.73 | 9949.3 | 59175
8.3086 | 670.73 | 10000 | 59509
7.8343 | 670.73 | 10051 | 59842
7.36 | 689.82 | 10102 | 60175
6.86 | 689.82 | 10164 | 60536
6.36 | 689.82 | 10226 | 60897
5.86 | 689.82 | 10288 | 61258
5.36 | 702.52 | 10351 | 61619
4.93 | 702.52 | 10397 | 61935
4.5 | 702.52 | 10639 | 62251
4.06 | 702.52 | 10686 | 62575
3.62 | 702.52 | 10734 | 62898
3.145 | 702.52 | 10785 | 63247
2.67 | 702.52 | 10836 | 63596
2.195 | 702.52 | 10887 | 63945
1.72 | 702.52 | 10938 | 64294
1.62 | 702.52 | 11020 | 64368
1.08 | 702.52 | 11467 | 64765
0.54 | 746.37 | 11914 | 65163
0 | 746.37 | 12374 | 65585
-0.38 | 746.37 | 12698 | 65882
-0.92 | 746.37 | 13159 | 66305
-1.46 | 762.27 | 13619 | 66729
-1.9657 | 762.27 | 14041 | 67134
-2.4714 | 762.27 | 14463 | 67540
-2.9771 | 762.27 | 14885 | 67946
-3.4829 | 762.27 | 15307 | 68353
-3.9886 | 762.27 | 15728 | 68760
-4.4943 | 762.27 | 16150 | 69167
-5 | 778.27 | 16572 | 69575
-5.5 | 778.27 | 16994 | 69986
-6 | 778.27 | 17425 | 70398
-6.5 | 778.27 | 17865 | 70810
-7 | 778.27 | 18313 | 71223
-7.5 | 778.27 | 18770 | 71636
-8 | 943.25 | 19236 | 72049
-8.4779 | 943.25 | 19684 | 72524
-8.9557 | 943.25 | 20141 | 72998
-9.4336 | 943.25 | 20606 | 73473
-9.9114 | 943.25 | 21080 | 73949
-10.3893 | 943.25 | 21563 | 74425
-10.8671 | 943.25 | 22054 | 74901
-11.345 | 1013.6 | 22554 | 75377
-11.8019 | 1013.6 | 23036 | 75866
-12.2587 | 1013.6 | 23517 | 76354
-12.7156 | 1013.6 | 23998 | 76843
-13.1725 | 1013.6 | 24479 | 77333
-13.6294 | 1013.6 | 24960 | 77823
-14.0862 | 1013.6 | 25441 | 78313
-14.5431 | 1013.6 | 25923 | 78803
-15 | 1222.9 | 26404 | 79294
-15.5 | 1222.9 | 26927 | 79936
-16 | 1222.9 | 27451 | 80578
-16.5 | 1222.9 | 27975 | 81221
-17 | 1222.9 | 28498 | 81864
-17.5 | 1222.9 | 29022 | 82508
-18 | 1222.9 | 29545 | 83151
-18.5 | 1222.9 | 30069 | 83795
-19 | 1222.9 | 30592 | 84439
-19.5 | 1222.9 | 31116 | 85084
-20 | 1222.9 | 31639 | 85728
-20.5 | 1222.9 | 32163 | 86373
-21 | 1222.9 | 32687 | 87018
-21.5 | 1222.9 | 33210 | 87663
-22 | 1222.9 | 33734 | 88309
-22.5 | 1222.9 | 34257 | 88954
-23 | 1222.9 | 34781 | 89600
-23.5 | 1222.9 | 35304 | 90246
-24 | 1359.7 | 35828 | 90892
-24.4714 | 1359.7 | 36325 | 91565
-24.9429 | 1359.7 | 36822 | 92239
-25.4143 | 1359.7 | 37320 | 92913
-25.8857 | 1359.7 | 37817 | 93587
-26.3571 | 1359.7 | 38314 | 94261
-26.8286 | 1359.7 | 38811 | 94935
-27.3 | 1680.9 | 39309 | 95609
-27.8143 | 1680.9 | 39863 | 96510
-28.3286 | 1680.9 | 40417 | 97411
-28.8429 | 1680.9 | 40971 | 98311
-29.3571 | 1680.9 | 41525 | 99212
-29.8714 | 1680.9 | 42080 | 100110
-30.3857 | 1680.9 | 42634 | 101010
-30.9 | 2153.6 | 43188 | 101920
-31.3429 | 2153.6 | 43655 | 102900
-31.7857 | 2153.6 | 44122 | 103890
-32.2286 | 2153.6 | 44589 | 104870
-32.6714 | 2153.6 | 45056 | 105860
-33.1143 | 2153.6 | 45524 | 106840
-33.5571 | 2153.6 | 45991 | 107830
-34 | 2626.3 | 46458 | 108810
-34.3 | 2626.3 | 46772 | 109620
-34.6 | 2608.4 | 47087 | 110430
-35.1 | 2542.7 | 47143 | 111770
-35.6 | 2429.2 | 47199 | 113080
-36.1 | 2279.8 | 47255 | 114320
-36.6 | 2099.5 | 47311 | 115500
-37.1 | 1890.4 | 47367 | 116580
-37.6 | 1650.8 | 47422 | 117550
-38.1 | 1380.2 | 47478 | 118410
-38.6 | 1066.1 | 47534 | 119130
-39.1 | 713.89 | 47590 | 119690
-39.6 | 343.19 | 47646 | 120080
-40.6 | 44.895 | 47758 | 120280
-41.1 | -445.99 | 47814 | 120090
-41.6 | -856.37 | 47870 | 119680
-42.1 | -1280.6 | 47926 | 119070
-42.6 | -1716.8 | 47982 | 118230
-43.1 | -2157.8 | 48037 | 117180
-43.6 | -2604.2 | 48093 | 115900
-44.1 | -3054.3 | 48149 | 114390
-44.6 | -3498.9 | 48205 | 112660
-45.1 | -3938.9 | 48261 | 110710
-45.6 | -4376.1 | 48317 | 108540
-46.0922 | -4796.6 | 48371 | 106200
-46.5844 | -5199.1 | 48425 | 103660
-47.0766 | -5589.1 | 48480 | 100920
-47.5688 | -5991 | 48534 | 97990
-48.0609 | -6404.5 | 48588 | 94852
-48.5531 | -6799.4 | 48642 | 91520
-49.0453 | -7161.8 | 48696 | 88009
-49.5375 | -7490.3 | 48750 | 84335
-50.0297 | -7786.8 | 48805 | 80515
-50.5219 | -8053.1 | 48859 | 76563
-51.0141 | -8280.3 | 48913 | 72499
-51.5063 | -8465.3 | 48967 | 68344
-51.9984 | -8608.2 | 49021 | 64117
-52.4906 | -8699.9 | 49075 | 59846
-52.9828 | -8741.9 | 49130 | 55553
-53.475 | -8724.7 | 49184 | 51268
-53.9672 | -8647.6 | 49238 | 47021
-54.4594 | -8516.6 | 49292 | 42838
-54.9516 | -8336.4 | 49346 | 38744
-55.4438 | -8111.7 | 49401 | 34760
-55.9359 | -7848.9 | 49455 | 30905
-56.4281 | -7548.6 | 49509 | 27198
-56.9203 | -7211.4 | 49563 | 23657
-57.4125 | -6837.6 | 49617 | 20301
-57.9047 | -6427.1 | 49671 | 17146
-58.3969 | -5979.6 | 49726 | 14211
-58.8891 | -5494.5 | 49780 | 11515
-59.3813 | -4971.2 | 49834 | 9077.3
-59.8734 | -4408.9 | 49888 | 6916.1
-60.3656 | -3807.7 | 49942 | 5051
-60.8578 | -3164.7 | 49996 | 3502.6
-61.35 | -2486 | 50051 | 2288.5
-61.85 | -1989 | 50119 | 1303.9
-62.35 | -1459.2 | 50187 | 584.36
-62.85 | -899.79 | 50255 | 144.71
-63.35 | -310.25 | 50323 | 3.5829e-08