## Term sheet
Topic | Description/requirement
Site specific requirements
Wind turbine permitted dimensions | Maxmimum of: 140 meter rotor diameter, 135 meter hub height, 205 meter tip height, 26 meter foundation diameter, top foundation: 3 meters above ground level
Site suitability | Contractor to confirm the site suitability for the offered wind turbine in its proposal, taking into account turbulence resulting from the windturbines in the vincinity. Employer will provide wind data for this assessment. Contractor to assess the impact of the current windturbines on the expected lifetime of the new windturbine.
Wind turbine locations | Location: X: 188.045 Y: 510.041 Z: 2,0 Also see "wind turbine location on map"
Site | Both wind turbines are situated in an industrial area with limited space to access, store and assemble (large) components, construct and erect the main crane, and/or parking space. Contractor to show in his proposal the preferred method of construction and corresponding site layout.
Grid connection restrictions | Voltage level of grid (kV): 10, N.B.: Declared Voltage (Uc) is for 10 kV netten: Uc =10,5 kV Due to restrictions in available space, the application of a step-down transformer should be avoided.
Grid compliance | Windturbine should be fully compliant to the applicable gridcode and comply with the requirements for generator. The WTG shall be able to operate continuously in all ranges of active power, reactive power, frequency and voltage fluctuations as specified in the grid codes, Requirements for Generators (RfG) and EN-50160. Power quality aspects including voltage fluctuations, flickers, harmonics during normal and abnormal operation shall be measured, tested and documented as given in IEC 61400-21. The Contractor shall avoid voltage disturbance in the array network due to transformer inrush currents from the WTGs. The Contractor shall evaluate these inrush currents based on data as supplied by the grid operator and/or Employer on request.
Certification product | Windturbine should be fully IEC 61400-1 type certified in accordance with the certification process as set out in the IEC 61400-22 or OD501.
Scope turbine supply agreement (TSA)
Contract format | Fidic Yellow 1999, T&C to be negotiated
Delivery scope | Transport, delivery, construction, commissioning and testing of one (1) certified wind turbine generator (WTG), including one (1) SCADA system+windfarm controller. Contractor optionally to provide a proposal for BoP-C and/or BoP-E works. The windturbine will have its own grid connection.
Wind turbine mandatory options | Aviation lights on nacelle and tower (including preparation ADLS and infrared lighting), shadow flicker control system, ice detection system.
Defect Notification Period (DNP) | 2 years, with option to extend to 5 years
Delay liquidated damages | Applicable.
Power curve warranty | Applicable during DNP
Noise curve warranty | Applicable during DNP
Securities/guarantees | Parent Company Guarantee Advance Payment Security Performance Security until end of DNP
Escrow agreement | Escrow agreement included as a schedule under the Contract.
Direct Agreement | Contractor to confirm willingness to enter into a Direct Agreement
Scope maintenance and service contract (MSA)
Contract format | supplier specific format, T&C to be negotiated.
Delivery scope | Full service maintenance and operation of the scope supplied under the TSA. This includes both scheduled as unscheduled maintenance, monitoring and remedying any blade erosion. The scope includes all for the execution of the Works required parts, labour, other personnel, materials, equipments (such as cranes), tools, consumables (such as fuel), utilities, security etc. The Contractor is responsible for the availability and replacement of any part and/or component of the WTG during the design lifetime of the WTGs. The works includes all for the execution of the Works required transportation, handling and storage. The works includes all for the execution of the Works required Health, Safety, Environment and Quality management The duration of the Maintenance Service Agreement is 15 years, with a possibility for the Employer to extend with 5 additional years.
Availability warranty windturbine | At least 97%. Contractor to include Availability Warranty, definition of Availability and calculation of Availility to the Offer, definition and calculation to be agreed between Parties
Compensation for non-avaiability | LD fee per MWh will be the PPA price (incl. GoOs) + any subsidy. T.b.d.
Payment | Quarterly payments of 25% of the annual MSA fee
Indexation | Only index for Labour costs and Materials with fixed weighting factors; related to relevant public indices
Offsetting | The Employer has the right to withhold MSA fee payments in the event the windturbine does not perform for a prolonged period of time and the liquidated damages cap is reached. The Employer has the right to set off the availability liquidated damages to the MSA fee quarterly payments. The Employer will resume with the MSA fee payments when the windturbine is restored to the desired state.
Contract term | The duration of the MSA is 15 years, with a possibility for the Employer to extend with 2 additional 5-year periods (so option for 16-20 and 21-25 years).
Direct Agreement | Contractor to confirm willingness to enter into a Direct Agreement