## TJEK LISTE (hidden)
TJEK LISTE
Driftsdata
At investeringen ændrer på NPV
At serviceaftale ændrer på NPV.
At kompressorarbejdet ændrer på NPV.
Varmepumpeberegning
Tabel til hældning
Dellastpunkter
Tabel til graf og beregninger
tjek hældningen passer med temperaturerne
Systemberegning
Afskrivningsperiode
At spidslast dækker varmebehov i reference
krydstjek af beregning med EnergyPRO
Produktionsomkostninger

## Operating data
The tenderer is required to complete ALL the green cells |  |  |  | Warmtenet Muiderberg | Warmtenet Muiderberg
All orange cells are pre defined. |  |  |  | HP01 - Lot A | HP01 - Lot A
All blue cells are calculated values |  |  |  | Date/rev.: | Date/rev.: | 26.08.2026 | rev 3.0 | The gasprice (reference case) has been adjustes to represente the expected future increase
See section 8 in document 0.3 and section 6.2 in document 4.1 for definitions.
Tenderer
Date for filling out
Total tender amount 1) |  |  | EUR
Price for complete service agreement for 5 years1) 3) |  |  | EUR
Total tender amount without service argreement 2) |  | 0 | EUR
Heat source: Water
| This number must be minimum 3100 kW |  | LAKE | LAKE | LAKE | LAKE | LAKE | LAKE | LAKE | LAKE
Nominal operating point
| Operating point |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
| Load |  | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
| Weight (for techno-economic optimization) |  | 23.9% | 24.59% | 8.285% | 3.225% | 15.93% | 16.39% | 5.523% | 2.15%
Cold side, intermediate circuit
| Inlet temperature | °C | 4 | 8 | 17 | 22 | 4 | 8 | 17 | 22
| Outlet temperature | °C | 1 | 4 | 11 | 16 | 1 | 4 | 11 | 16
| Temperature decrease | K | 3 | 4 | 6 | 6 | 3 | 4 | 6 | 6
| Water flow (max. 500 m³/h available) | m³/h | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling capacity | kW
| Pressure loss | kPa
| Evaporation temperature, heat pump | °C
Hot side, district heating
| Return temperature | °C | 50 | 50 | 50 | 50 | 35 | 35 | 35 | 35
| Supply temperature | °C | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72
| Temperature increase | K | 22 | 22 | 22 | 22 | 37 | 37 | 37 | 37
| Heat capacity 1) | kW
| Flow | m³/h | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pressure loss | kPa
Electricity consumption
| Compressors | kW
| Electrical power for pump(s), cold side | kW
| Electrical power for pump(s), warm side | kW
| All other electricity consumption | kW
| In total 1) | kW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Efficiency
| COP-warm | - | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
| LMTD cold | K | 275.6473 | 279.1452 | 287.1396 | 292.1397 | 275.6473 | 279.1452 | 287.1396 | 292.1397
| LMTD warm | K | 334.0293 | 334.0293 | 334.0293 | 334.0293 | 326.3004 | 326.3004 | 326.3004 | 326.3004
| Lorenz-COP | - | 5.7214 | 6.0861 | 7.1237 | 7.9741 | 6.4419 | 6.9197 | 8.3323 | 9.5519
| Lorenz-efficiency 4) | % | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Other calculations
| Heat output 4) | kW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat loss (should NOT be negativ) | kW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Varme minus el | kW | 0 | 0 | 0 | 0 |  |  |  | 0
| Beregnet varmetab | kW | 0 | 0 | 0 | 0 |  |  |  | 0
Net Present Value
|  | #DIV/0! | Nominal operating point 1: EUR
1) These lines affect the net present value
2) This price is included as an investment in the net present value calculation.
3) This price is used for the calculation of O&M
4) These are used for calculating penalties/bonuses in the guarantee tests
Effektforbrug | 11

## System calculation (hidden)
Input
| 60% |  |  |  | 40%
Heat pump | 0.39832 | 0.40984 | 0.13808 | 0.053756 | 0.39832 | 0.40984 | 0.13808 | 0.053756
Operating point | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 |  | In Danish
Vægtning | 23.9% | 24.59% | 8.285% | 3.225% | 15.93% | 16.39% | 5.523% | 2.15% | Weighted average |  |  |  | Heat Demand
COP-varm | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 7.45 |  | Value | Unit | Comment
[13 empty] | # small consumers | 1336 | - | All total potential consumers
Operation | [9 empty] | Drift | Numbers in DKK |  | Connecrion rate SC | 80% | -
O&M | #DIV/0! | EUR/MWh heat | 4200 hours of operation each year |  |  | THN - keep the 4200 hours this is in line with energypro and the documents |  |  |  | D&V [kr./MWh] | #DIV/0! | kr/MWh_varme | # large consumers | 18 | - | 18 out of 22
Tariffs & Distribution Costs | 69 | EUR/MWh elec | utrecht | [6 empty] | Afgifter | 514.05 | kr./MWh el | Heat Demand SC | 10.8056 | MWh/yr | From BuCa
Electricity | 80 | EUR/MWh elec | higher boundary | [6 empty] | Brændsel pris | 596 | kr./MWh el | Heat Demand LC | 32.7778 | MWh/yr | From BuCa
Yearly heat production from heat pump | 15173.7222 | MWh | [7 empty] | Årlig varmeproduktion | 15173.7222 | MWh | Total Heat Demand | 12138.9778 | MWh/yr | 80% CR
[13 empty] | Heat losses | 20% | -
[13 empty] | Total heat Production | 15173.7222
Other input | [9 empty] | Øvrige input
Economic lifet ime | 15 | years | OK | [6 empty] | Teknisk levetid [år] | 15 | år
Interest | 3.5% | p.a. | [7 empty] | Real rente [%] | 3.5% | p.a.
Service agreement term | 5 | years |  | don't change this back to 10 yr if we do that that calculations of O&M is wrong | [5 empty] | Løbetid serviceaftale [år] | 5 | år
Other client costs | 0 | EUR | [7 empty] | Bygherres øvrige omkostninger [DKK] | 0 | kr.
[10 empty] | Årlig driftsomkostning, reference | 10173980.75 | kr/år
Annual operating cost, reference | 1365635 | EUR/year | utrecht
Calculations and result
HP FLH | #DIV/0! | FLH | [7 empty] | VP fuldlasttimer | #DIV/0! | FLH
Heat production cost | #DIV/0! | EUR/MWh | [7 empty] | Produktionspris | #DIV/0! | kr./MWh varme
Yearly electricity consumption | #DIV/0! | MWh | [7 empty] | Årlig elforbrug | #DIV/0! | MWh el
Yearly O&M cost | #DIV/0! | EUR/year | [7 empty] | Årlig D&V | #DIV/0! | kr./år
Yearly electricity cost | #DIV/0! | EUR/year | [7 empty] | Årlig elomkostninger | #DIV/0! | kr./år
Yearlig production cost, heat pump | #DIV/0! | EUR/year | [7 empty] | Årlig produktionsomkostninger | #DIV/0! | kr./år
NPV
Gross investment | 0 | EUR | [7 empty] | Brutto investering | 0 | kr.
First-year capital costs | 0 | EUR | [7 empty] | 1. års kapitalomkostninger | 0 | kr.
Operating costs without heat pump | 1365635 | EUR/year | [7 empty] | Driftsomkostninger uden VP | 10173980.75 | kr./år
Operating costs with heat pump | #DIV/0! | EUR/year | [7 empty] | Driftsomkostninger med VP | #DIV/0! | kr./år
Operating cost savings | #DIV/0! | EUR/year | [7 empty] | Driftsbesparelse | #DIV/0! | kr./år
Simple payback period | #DIV/0! | Years | [7 empty] | Simpel tilbagebetalingstid | #DIV/0! | år
First-year net savings | #DIV/0! | EUR/1.year | [7 empty] | 1. års nettobesparelse | #DIV/0! | kr./1. år
Internal rate of return (IRR) | #VALUE! | p.a. | [7 empty] | Intern rente | #VALUE! | p.a.
Net present value (NPV) | #DIV/0! | EUR | #DIV/0! | [6 empty] | Nutidsværdi | #DIV/0! | kr.
Year | [9 empty] | År
0 | 0 | 0 | [7 empty] | 0 | 0 | 0
1 | #DIV/0! | #DIV/0! | [7 empty] | 1 | #DIV/0! | #DIV/0!
2 | #DIV/0! | #DIV/0! | [7 empty] | 2 | #DIV/0! | #DIV/0!
3 | #DIV/0! | #DIV/0! | [7 empty] | 3 | #DIV/0! | #DIV/0!
4 | #DIV/0! | #DIV/0! | [7 empty] | 4 | #DIV/0! | #DIV/0!
5 | #DIV/0! | #DIV/0! | [7 empty] | 5 | #DIV/0! | #DIV/0!
6 | #DIV/0! | #DIV/0! | [7 empty] | 6 | #DIV/0! | #DIV/0!
7 | #DIV/0! | #DIV/0! | [7 empty] | 7 | #DIV/0! | #DIV/0!
8 | #DIV/0! | #DIV/0! | [7 empty] | 8 | #DIV/0! | #DIV/0!
9 | #DIV/0! | #DIV/0! | [7 empty] | 9 | #DIV/0! | #DIV/0!
10 | #DIV/0! | #DIV/0! | [7 empty] | 10 | #DIV/0! | #DIV/0!
11 | #DIV/0! | #DIV/0! | [7 empty] | 11 | #DIV/0! | #DIV/0!
12 | #DIV/0! | #DIV/0! | [7 empty] | 12 | #DIV/0! | #DIV/0!
13 | #DIV/0! | #DIV/0! | [7 empty] | 13 | #DIV/0! | #DIV/0!
14 | #DIV/0! | #DIV/0! | [7 empty] | 14 | #DIV/0! | #DIV/0!
15 | #DIV/0! | #DIV/0! | [7 empty] | 15 | #DIV/0! | #DIV/0!
|  | #DIV/0! | [9 empty] | #DIV/0!
|  | #DIV/0! | [9 empty] | #DIV/0!
| -700000 | Indledende omkostninger for en forretning
| 12000 | Nettoindtægt for det første år
| 12000 | Nettoindtægt for det andet år
| 12000 | Nettoindtægt for det tredje år
| 12000 | Nettoindtægt for det fjerde år
| 12000 | Nettoindtægt for det femte år
-49.26%
Note on B17: [Trådet kommentar] Din version af Excel lader dig læse denne trådede kommentar. Eventuelle ændringer vil dog blive fjernet, hvis filen åbnes i en nyere version af Excel. Få mere at vide: https://go.microsoft.com/fwlink/?linkid=870924 Kommentar: Realrente: lånerente-inflation

## Konstanter (hidden)
Enhed
Kelvin | 273.15 | K

## Bodsudregning (hidden)
Størrelsesfaktor | 100%
El-faktor | 100%
Effekt |  | kW
Lorenz | #REF! | -
Nutidsværdi | #DIV/0! | kr
Effekt / [kW] |  |  | Størrelsesfaktor
| 0 | 99% | 100% | 101%
| 101% | 0 | 0 | 0
El-faktor | 100% | 0 | 0 | 0
| 99% | 0 | 0 | 0
Lorenz |  |  | Størrelsesfaktor
| #REF! | 99% | 100% | 101%
| 101% | #REF! | #REF! | #REF!
El-faktor | 100% | #REF! | #REF! | #REF!
| 99% | #REF! | #REF! | #REF!
Nutidsværdi
Nutidsværdi / [kr.] |  |  | Størrelsesfaktor |  | kr./%-point
| #DIV/0! | 99% | 100% | 101%
| 101% | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
El-faktor | 100% | #DIV/0! | #DIV/0! | #DIV/0!
| 99% | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[5 empty] | #DIV/0! | kr./ 0,01 %-point i gennemsnit
[5 empty] | #DIV/0! | kr./ 0,01 %-point i gennemsnit efter et rimelighedsprincip