## Blad1
Marketconsultation Mobile Power Supply
Requirements electrical power
Case 1 |  |  | Case 2 |  |  | Case 3
Voltage | 690 | V AC | Voltage | 400 | V AC | Voltage | 400 | VAC
Required maximum Power | 1000 | kW | Required maximum Power | 42 | kW | Required maximum Power | 130 | kW
Required minimum Power | 200 | kW | Required minimum Power | 14 | kW | Required minimum Power | 10 | kW
Maximum ramp up speed 0 - 500 kW +/- 30 seconds (start-up) |  |  | Maximum ramp up speed 0 - 50 kW +/- 30 seconds (start-up) |  |  | Speed power consume by system error | 10 - 120 kW in few seconds for 5 minutes,
Maximum ramp down speed 900 - 0 kW +/- 10 seconds (unit trip) |  |  | Maximum ramp down speed 50 - 0 kW +/- 10 seconds (unit trip) |  |  |  | after 5 minutes the power consume will drop to 60 kW for approx 15 minutes,
after in total 20 minutes the power consume will established at 15 or 25 kW
Auxillary voltage | 400 | V AC | Auxillary voltage | 400 | V AC | The biggest Power use comes from the electrical heaters
Required maximum Power | 30 | kW | Required maximum Power | 15 | kW
Required minimum Power | 4 | kW | Required minimum Power | 3 | kW