## FMECA Questionnaire
FMECA Questionnaire |  |  | Total maximum points | 80
Category | Question | Possible answers | Answer Tenderer | Maximum points
Materials used | What polymers are used in the LV strips: mention the name/function of the part, size (in cm for length, width and hight), polymer name or abbreviation (for instance PC, PP, POM, PA 6.6, PA 11, PE, ABS). Submit a photo and material specification of the polymers.
| Are flammable materials used in the LV strips? | Yes / No
What are the flammable parts: mention the name/function of the part, size (in cm for length, width and hight), material (for instance PC, PP, POM, wood).
Fragility | Are any parts breakable other than the mentioned polymers? | Yes / No
What parts other than polymers are breakable: mention the name of the part, size (in cm for length, width and hight), material name (for instance porcelain)
| Which polymers or other breakable parts suffer from tension during operations like placing fuses or switching: mention the name of the part where the tension is, the material type and the spot that will suffer from force during operations? | PA 11 en PA 12 - 10 points PP glass fiber reinforced - 10 points PA 6.6 - 5 points PBT - 5 points PC - 0 points PP - 0 points Pertinax - 0 points POM - 0 points |  | 10
| Which polymers or other breakable parts suffer from tension during assembly / mounting like connecting LV cables or mounting the LV strip on the LV rack: mention the name of the part where the tension is, the material type and the spot that will suffer from force during assembly or mounting? Also mention what the torque in Nm is for mounting screws and bolts. | PA 11 en PA 12 - 10 points PP glass fiber reinforced - 10 points PA 6.6 - 5 points PBT - 5 points PC - 0 points PP - 0 points Pertinax - 0 points POM - 0 points |  | 10
Flammability (LOI) | How flammable is the LV strip in the vertical direction (LOI > 21 or > 35) if there is a fire at the bottom of the LV rack? Explanation: An indicator for flammability is the Limiting Oxigen Index (LOI). The LOI mentions if a polymer will spread the fire by continuing burning. If the LOI is higher than 35 than the fire will normally stop. | None of the LV-strip parts will continue burning in the vertical direction (LOI > 35)/ 5 points The LV-strip parts will burn in the vertical direction (21 < LOI < 35) / 0 points |  | 5
Corrosion by moisture and water | Are primary conductors like rail and contacts treated to withstand corrosion from moisture and water for instance by paint, coating, tinned, silverd, ..? | Silvered / 5 points Tinned / 2 points Other (e.g. blank, coated, painted) / 0 points |  | 5
Which parts are treated against corrosion from moisture and water?
| How well treated are the parts against corrosion from moisture and water? | Multiple hours per day the primary parts will withstand moisture and the relative humidity can frequently be higher than 95 %. / 5 points Some hours per month the primary parts will withstand moisture and the relative humidity can sometimes be higher than 95 % but should normally be below 95 %. / 2 points The primary parts should not be used in humid environment. The relative humidity should be lower than 85 %. / 0 points |  | 5
| What is the long term effect of moisture on the primary parts. (RH > 95 %, often moisture on parts)? | Bad contact due to corrosion: Yes / No? Yes / 0 points No / 5 points |  | 5
|  | Electrical isolation lower than 400 V: Yes / No? Yes / 0 points No / 5 points |  | 5
Other: ..
Contact pressure | How is the contact pressure on the fuse made​​. | Spings (coil), spring (horse shoe), other construction: ..
| What kind of material is used? | Galvanised steel / 10 points Steel or other / 0 points |  | 10
| What is the intended life of the part that is making the contact pressure. | Less than 30 years / 0 points Minimum of 30 years / 3 points Minimum of 40 years / 7 points Minimum of 50 years / 10 points |  | 10
| Will the contact pressure be less due to fatigue or corrosion by oxidation or corrosion by curing or something else? | No limited live time, due to fatigue, corrosion by oxidation, corrosion by moisture, ...
Cable connection | When a 240 mm2 sector shaped conductor of a LV cable is connected to the LV strip, what is the distance to the terminals of the other phases? Is there sufficient space to prevent a short-circuit? | < 0.5 cm / 0 points 0,5 <> 1 cm / 2 points 1 <> 2 cm / 4 points > 2 cm / 5 points |  | 5
Maintainability | Are hotspots visible with an infrared (IR) camera or is it blocked by sheets or parts that can't be removed without switching off the power? | Primary connections as terminals, transformer connection, railcontact can be inspected with an IR-camera without switching off / 10 points Some of the primary connections are inspectable with an IR-camera without switching off / 5 points None of the primary connections are inspectable with an IR-camera without switching off / 0 points |  | 10
How are the connections of primary conductors visible? Describe if they all are visible without removing parts or what is needed to make primary connections visible.

## User convenience
User convenience |  | Total maximum points | 20
Category | Question | Possible answers | Maximum points
User convenience | Is it possible to align the LV-strip on a rail during assembly while energized (for aligning mounting holes)? | Scale of 0-2-4-6-8-10 | 4
| Is it possible to set the switch cover of the fuse to “standby”? | Yes / No | 1
| Is it possible to block a LV-strip with a signal board 'Do not switch'? | Yes / No | 1
| Is it possible to integrate the measuring core into the LV-strip (according to the measuring core specifications)? And is it possible to wire the measuring cores with the use of a RJ45 connector? | Yes, compatible with Enexis standard (RJ45 connector): 1 Yes, different technical solution : 0,5 No: 0 | 1
| How is the mounting of the LV-strip type NH2? | Scale of 0-2-4-6-8-10 | 1
| How is the mounting of the LV-strip type NH3? | Scale of 0-2-4-6-8-10 | 1
| How is the mounting of two 150 mm2 aluminium cables? | Scale of 0-2-4-6-8-10 | 1
| How is the mounting of a 240 mm2 aluminium cable? | Scale of 0-2-4-6-8-10 | 1
| How is the mounting of cables used for public lighting? | Scale of 0-2-4-6-8-10 | 1
| How is the (dis)assembly of the LV-strip outgoing feeder for 400A), if it has to be mounted while energized? | Scale of 0-2-4-6-8-10 | 1
| How is the (dis)assembly of the LV-strip NH3 (transformer feeder for 1000A)? | Scale of 0-2-4-6-8-10 | 1
| How do you experience the (dis)assembly of the LV-cable when the neighboring LV-strips are energized? (VWI-E23) | Scale of 0-2-4-6-8-10 | 3
| Are the fuses easy to remove/replace from the fuse holders? | Scale of 0-2-4-6-8-10 | 1
| How is the switching of the NH2 LV-Strip? | Scale of 0-2-4-6-8-10 | 1
| How is the switching of the NH3 LV-Strip? | Scale of 0-2-4-6-8-10 | 1