## ItT - Reply format Price Sheet
Invitation to Tender DALI - Reply format Price sheet
Please fill out the blue cells
Tenderer Name:
A. Price standard configuration
Price Euro (exclusive VAT)
Total price one DALI-box
Price one external (mobile) display, if appplicable (refer Annex 3: Technical Specification, 1.4.3)
B. Price of tools/systems
Price Euro (exclusive VAT)
Central software tooling/licence for minimal 10 users (refer Annex 3: technical Specification, 4.2.2 and 4.2.3 and Annex 5: Security Requirements, SMR.02 and SMR.03)
Hardware /server(s) to run central software tools, including installation and commissioning (refer Annex 3: technical Specification, 4.2.2 and 4.2.3)
C. Price of initial engineering/installation (only if thought applicable by tenderer)
| Specification | Price Euro (exclusive VAT)
Additional initial costs if applicable (refer Annex 3: technical specification, 5.4.1)
D. Price of Training
Price Euro (exclusive VAT)
Expert Training: 2 training courses in the Netherlands for system-engineers / total 10 system-engineers (refer Annex 3: Technical Specification, 5.3.1)
Basic Training: 2 training courses in the Netherlands / total 16 field technicians (refer Annex 3: Technical Specification, 5.3.2)
E. Price of individual components
Price Euro (exclusive VAT)
Last Gasp power backup (refer Annex 3: Technical Specification, 1.6.5)
F. Price of support
Price Euro (exclusive VAT)
Support per hour on site, all costs included (refer Annex 3: Technical Specification, 5.4.4)
Future software developpment on request per hour (refer Annex 3: Technical Specification, 5.4.2)
G. Price of Support contract/SLA
Price Euro (exclusive VAT)
Yearly support costs (refer Annex 3: Technical Specification, 5.4.1 until 5.4.6)
H. Mainenance costs
Failure rate percentage
Cumulatively failure rate over 10 Years of service (refer. Annex 3: Technical Specification, 3.2.2)

## ItT - Reply format specs
Invitation to Tender DALI - Reply format Specs
Please fill out the blue cells
Tenderer Name:
Ref. | Requirement type AC=Awarding Crit. MR=Minimum Req. | Requirement | Requirement description | Reply-format | Valuation category (if AC) | Max. score | Assessment method | Reply
[8 empty] | Yes/No | Specification
Technical Specification (Refer Annex 3)
1. | Hardware requirements
1.1 | Enclosure
1.1.1 | MR | Enclosure | The weight of the DALI-box must be maximum 10kg (excluding Last-gasp components). | Yes/No
1.1.2 | MR | Enclosure | Enclosure: Plastic. There is no specific color-requirement for the enclosure itself. | Yes/No
1.1.3 | MR | Enclosure | Enclosure must have protection class ≥ IP44, excluding outside part of connectors. | Yes/No
1.1.4 | MR | Enclosure | The applied materials must comply with the Limiting Oxygen Index (LOI). This is an indicator of the combustibility of a material. The plastic materials used must not have a lower LOI than 35. | Yes/No
1.1.5 | MR | Enclosure | The minimum strength resistance is IK07 according to EN 50102. | Yes/No
1.1.6 | MR | Enclosure | The external dimensions of the DALI-box shall be less than or equal to: 300x300x180 mm (w*h*d). | Yes/No
1.1.7 | AC | Enclosure | Smaller dimensions of the DALI-box (refer 1.1.6) is desirable and will be valued. | Specify dimensions | Technical specification | 20 | Fixed, Linear (16,2 liter or more = 0; 6 liter or less = 20; linear score in between)
1.1.8 | MR | Enclosure | The DALI-box is fitted with a hinged, transparent front. Securing front over screws is accepted. | Yes/No
1.1.9 | MR | Enclosure | The DALI-box must be easy to mount by one technician. This implies among other things: - minimum 3 mounting brackets (no mounting-holes inside box); - mounting brackets must facilitate fixation of box; | Yes/No
1.1.10 | MR | Enclosure | The DALI-box must be accompanied with the following (basic) information: - Connection-diagram of main components and slots printed on sticker or paper (paper stored inside box). | Yes/No
1.1.11 | MR | Enclosure | On the front of the cabinets the following information is made available (over sticker(s) or print(s) or plate(s)): - Manufacturer / Type box - Serial Number (identical to DALI-box serial# what is used for autentication) - QR-code (identical to DALI-box ID what is used for autentication) - Production Year - Indication of specified signal-lights or status-indicators | Yes/No
1.1.12 | MR | Enclosure | The front of the DALI-box must be provided with a warning that says "Melden BVC voor openen". | Yes/No
1.1.13 | MR | Enclosure | On the inside of the DALI-box the following information is made available over sticker: - ICCID-code used Simcard. | Yes/No
1.1.14 | MR | Enclosure | Opening the DALI-box must in all cases be identified over a electromechanical door contact. | Yes/No
1.2 | Communication protocols
1.2.1 | MR | Communication protocols | The DALI-box must support at least one of two below mentioned protocols for the exchange of data with central OT-domain: • IEC 60870-5-104 protocol implementation. This implementation must meet Enexis 104 PID (refer Annex 6). Adresses must be definable based on Asdu and CASDU. • JSON over WS implementation according to Annex 7. Implementation of both protocols is also allowed. | Yes/No. Please specify what protocol is supported.
1.2.2 | MR | Communication protocols | Evidence for the correct deployment of protocols by Tenderer must be proved through conformance test certificates after awarding. In addition, Enexis maintains the right to subject the offered system(s) to a 'conformance' test by an independent executive authority. Any negative findings are resolved without charge by Tenderer within 2 weeks. Tenderer will be (cost-) responsible for retest(s) in case of any findings. | Yes/No
1.2.3 | MR | Communication protocols | For verification of proper communication between CPU/RTU and central data collection system, Enexis preserves the right to subject the offered system(s) to an "interoperability test" after awarding. Any negative findings are resolved without charge by Tenderer within 2 weeks. Tenderer will be (cost) responsible for retest(s) in case of any findings. Remark: this Minimum Requirement is only relevant in case of use IEC60870-5-104 Protocol. | Yes/No
1.2.4 | MR | Communication protocols/SFTP | DALI-box must support up/download of measurement data, system logfiles and/or configuration files by using SFTP. Exact choice depends on 104 or JSON. Refer annex 2: Accompanying letter for details using 104 and/or JSON | Yes/No
1.2.5 | MR | Communication protocols/SSH | The DALI-box must support remote secure shell using SSH | Yes/No
1.3 | I/O
1.3.1 | MR | Hardwired I/O | The DALI box must facilitate minimum 6 active Digital Inputs: • 3 active DI for reading status Short circuit indicator contacts (NO) • 1 active DI for reading status internal mechanical door contact DALI-box (NO) • 1 active DI for reading status mechanical door contact Secondary Substation (NO) • 1 spare active DI (NO) | Yes/No
1.3.2 | MR | Hardwired I/O | Digital Inputs are used to read position reports and status signals. a. Power supply for reading external potential-free contacts (NO) must be supported over max. 24 VDC. b. In case of status signals, a dead band in between must be supported to identify logical "0" and logical "1". c. Signals with a pulse duration > 100 msec. must be handled unequivocally. d. Time labels assigned to events must not deviate by more than 100 msec compared to RTU time. e. Time labels for reports and alarms must be handled in such a way that they remain uniquely identifiable within the system. | Yes/No
1.3.3 | MR | Digital I/O | The DALI-box must support monitoring of transformer load variables (refer 2.3.2) and must be expandable over extension boxes (extension-boxes out of scope tender) to monitor up to 12 outgoing LV-feeders , based on Modbus protocol. | Yes/No.
1.3.4 | MR | Digital I/O | The DALI-box must support a Modbus RTU master interface, based on: - Minimum speed of 9600 Baud - Mode settings configurable by Enexis - Polling frequency of ≥ 0.1 Hz - To be polled registers of Modbus-IED's can be remotely configured by Enexis. - Connecting Modbus over USB is not acceptable. | Yes/No
1.3.5 | AC | Digital I/O | The DALI-box shall support a Smart meter P1-port input in order to read smart meter data of public street lights (Consumption counters, Power flow and Tariff-status). For specifications P1-port refer to Annex 13, DSMR v5.0.2 Final P1. | Yes/No | Technical specification | 10 | Fixed (Yes: 10; No: 0)
1.3.6 | MR | Hardwired I/O | The DALI box must facilitate minimum 3 Digital Outputs: • 1 DO for control of (contactor) Evening/morning-lights (1); • 1 DO for control of (contactor) Night-lights (2); • 1 DO for control of Tariff (3). | Yes/No
1.3.7 | MR | Hardwired I/O | Digital Outputs must be: a. potential-free, capable of switching 230VAC b. suitable for loads of 1 A (DO 1 and 2) class AC14 and 16A (DO 3) class AC2; | Yes/No
1.3.8 | MR | LAN-port | The DALI box must have an RJ45 interface that supports an ethernet LAN connection, with below mentioned specification: a. The LAN connection must be disabled by default (only the WAN interface is active) and it must be possible to remotely activate the LAN connection. b. The DALI box application must contain functionality for the management of both communication mechanisms (WAN and LAN). This expecially applies to properly handling the timers and watch- dogs described in the WAN requirements document (Annex 4). | Yes/No
1.4 | Visual information
1.4.1 | MR | System information | The following system-information must be minimum visible on the outside of the DA box (over transparent front): a. general system-failure: yes/no (basis of which field technician can determine if system is working correctly). b. IP connection and/or data transfer over modem. c. connected to mobile network. And if applicable: d. low last gasp functionality (must indicate if last gasp unit needs replacement as a result of to low voltage and/or to rapid discharge). e. local Modbus communication failure (must indicate if one ore more Modbus IED's can not be reached/read as a result of defect IED, not properly configured IED or incorrect Modbus wiring). It's not acceptable that a user needs to go through menu (screen) options to get the desired information. | Yes/No
1.4.2 | MR | Status information | The following status-information must be clearly visible on the outside of the DALI box (over transparent front): a. Status DO's (active/not active; one LED for each DO is accepted) b. Status DI's (active/not active; one LED for each DI is accepted) It's not acceptable that a user needs to go through menu (screen) options to get the desired information. | Yes/No
1.4.3 | MR | Measurement information | All specified values of measurements (refer paragraph 2.3.2) must locally be visible (based on local data). This can be achieved over a fixed display inside enclosure or a separate (mobile) external display that can be temporarily connected to the DALI-box (internal connection; not over external connector). | Yes/No. Please specify solution provided. In case separate display, specify unit in Reply format price sheet.
1.5 | Connections
1.5.1 | MR | External connections | All below mentioned external connections must be positioned at the bottom of the DALI-box. External connections need to be supported over coded plastic connectors and external wires must be able to be connected without opening enclosure. | Yes/No
1.5.2 | MR | External connections | X1: Power supply and voltage input 230/400 VAC. Connector-type: Phoenix contact, SPC 5/5-STF-7,62 and DFK-PC 4/5-GF-7,62 series or equivalent. Refer to Accompanying letter annex 2: "External connector terminal definition". | Yes/No
1.5.3 | MR | External connections | X2: Current-sensor inputs. Connector-type: Phoenix contact, SPC 5/6-STF-7,62 and DFK-PC 4/6-GF-7,62 series or equivalent. Refer to Accompanying letter annex 2: "External connector terminal definition". | Yes/No
1.5.5 | MR | External connections | X3: Digital inputs. Connector-type: Phoenix contact, SPC 5/10-STF-7,62 and DFK-PC 4/10-GF-7,62 series or equivalent. Refer to Accompanying letter annex 2: "External connector terminal definition". | Yes/No
1.5.4 | MR | External connections | X4: Public street light and Tariff outputs. Connector-type: Phoenix contact, SPC 5/6-STF-7,62 and DFK-PC 4/6-GF-7,62 series or equivalent. Refer to Accompanying letter annex 2: "External connector terminal definition". | Yes/No
1.5.6 | MR | External connections | DALI-box must have minimum 3 cable-glands for entering external cables (e.g. external antenna cable, external Modbus-connection etc): • one cable gland M20. • two cable gland M16. | Yes/No
1.5.7 | MR | Internal connections | DALI-box must provide Modbus interface: minimal 1x 3 pole. No specific connector requirements (screw-connector accepted). Terminal assignment: Pin 1=TX+, 2=TX-, 3=Earth. This connector is meant to be available on the inside (NOT outside) of the enclosure. | Yes/No
1.5.8 | AC | Internal connections | DALI-box facilitates a Smart Meter interface (P1-port): RJ11 (6 PIN). For specifications P1-port refer to Annex 13, DSMR v5.0.2 Final P1. This connector is meant to be available on the inside (NOT outside) of the enclosure. | Yes/No | Technical specification | 5 | Fixed (Yes: 5; No: 0)
1.5.9 | MR | Internal connections | The DALI-box must provide an RJ45 interface that supports an ethernet LAN connection. This connector is meant to be available on the inside (NOT outside) of the enclosure. | Yes/No
1.5.10 | MR | Internal connections | The DALI-box must provide 24 VDC terminals to power external IED's (refer 1.6.4). This terimals are meant to be available on the inside (NOT outside) of the enclosure. | Yes/No
1.6 | (Emergency) Power supply
1.6.1 | MR | Power supply | The DALI-box must be suitable for a supply voltage of 230/400 VAC -10% to +10%. | Yes/No
1.6.2 | MR | Power supply | The 230/400 VAC supply must be internally additionally protected (glass fuse not accepted) in case protection provided by Enexis at power connection point over fuse 2A type GG is not sufficient. | Yes/No
1.6.3 | MR | Power supply | The DC voltage must be short-circuit and overload protected by an automatic fuse. | Yes/No
1.6.4 | MR | Power supply | The DC voltage must be sufficient to power the DALI-system and 3 external IED's. Power consumption IED's in total: 24VDC / 5W. | Yes/No.
1.6.5 | MR | Emergency power supply | The DALI-box must be prepared to add a last gasp emergency power supply (inside cabinet) afterwards. Remark: the last gasp functionality is not part of the standard DALI-box and will be ordered seperately. | Yes/No
1.6.6 | MR | Emergency power supply | The seperately to be offered last gasp functionality must be able to successfully transmit or process short circuit indicator position changes to the central system in case of power-failure. Last gasp functionality for 30 seconds after power-failure during lifetime is sufficient. Last gasp functionality must be designed for system power consumption and an additional 5W external power consumption (powering short circuit indicators during 30 seconds). | Yes/No
1.6.7 | MR | Emergency power supply | The seperately to be offered Last gasp functionality must have an design life of at least 12 years (based on 20 Degrees Celsius operating conditions). Last gasp functionality is maintenance free. | Yes/No
1.6.8 | MR | Emergency power supply | The seperately to be offered Last gasp power source (e.g. battery or powercap) must be connected with plugs in order to facilitate easy placement and replacement. | Yes/No
1.6.9 | MR | Emergency power supply | Temperature compensated loading of offered Last gasp power source must be facilitated, in case batteries are used for emercency power supply. | Yes/No
1.6.10 | AC | Emergency power supply | Enexis preferres few Last gasp power source replacements. Longer design life as stated in 1.6.7 are preferred and will be extra awarded. | Specify Last gasp power source solution and design life. | Technical specification | 15 | Fixed, Linear (15 = designlife 20 years or more; 0 = designlife 12 years or less; linear score in between)
1.6.11 | AC | Emergency power supply | Replacement/spare Last gasp power source units shall be stored in non-energized conditions for at least 2 months, without structural degrading of its capacity. Higher shelf times will be extra awarded. | Specify Shelf time for Last gasp power source units (based on recommendation of supplier). | Technical specification | 5 | Fixed, Linear (5 = shelftime 24 months or more; 0 = shelftime 2 months or less; linear score in between)
1.6.12 | MR | Emergency power supply | A general alarm (to trigger replacement) must be generated if Last gasp power source capacity decreases and is not able to perform as specified. | Yes/No
2. | System behaviour
2.1 | Power-up behaviour
2.1.1 | MR | Power-up behaviour | When starting up from a voltage-less state, the box must respond as if it were an initial start-up. The system must not end up in an undefined state. Invalid events/alarms and/or measurement-values during start-up must be suppressed. Digital Outputs must restore specified position (if public lights must be activated after start-up, this activation must be recovered). | Yes/No
2.1.2 | MR | System monitoring | The system must automatically generate a message via IEC 60870-5-104 or JSON if RTU, I/O-modules and/or IED's, or parts thereof, are lost. The individual alarms must be able to be transferred into a collective message in a simple manner. The desired functionality must be configured and/or parameterized through configuration/application-software. See Annex 2: Accompanying letter for details using 104 and/or JSON. | Yes/No
2.1.3 | MR | Watchdog | A configurable watchdog mechanism shall be supported by the DALI box ensuring correct functionality and co-existence with other implemented mechanisms/features. In case of any issues on device or network side which would result in loss of service and ability to communicate with central server, watchdog mechanism will ensure DALI box reset aiming to regain service. | Yes/No
2.2 | System-functionality
2.2.1 | Load management and related purposes
2.2.1.1 | MR | Timestamp | All measurements by RTU must be provided with a time stamp. | Yes/No
2.2.1.2 | MR | Accuracy | Accuracy of measurement data-chain must be ≤ 1% (excluding sensor). | Yes/No
2.2.1.3 | MR | Current-ratio | Only non-scaled values must be transmitted to central OT-system. Current-ratio of current transformers must be remotely configurable for RTU. | Yes/No
2.2.1.4 | AC | Connection-test | DALI-box is able to automatically verify correct connections of analog inputs (Voltage and Current-sensors). E.g. functionality supported by digital meter. | Yes/No | Technical specification | 10 | Fixed (Yes: 10; No: 0)
2.2.2 | Public Street Light control
2.2.2.1 | MR | Control | DALI-box must support a local astronomical clock. | Yes/No
2.2.2.2 | MR | Control | DALI-box must support a locally stored Public Street Light program. Available memory storage must be sufficient to store 9 programs. Each program can cover a time period of 1 year. Only 1 program is active. Programs are stored using the local timezone. | Yes/No
2.2.2.3 | MR | Control | Locally stored Public Street Light program must be centrally configurable/managable using JSON as descibed in Annex 7 or using a uploadable configuration file. Refer Annex 2: Accompanying letter for details using 104 and/or JSON. | Yes/No
2.2.2.4 | MR | Control | Public Street light program must support: • Fixed time basis for activation and de-activation for Evening/morning as well as Night-lights seperately. • Configurable offset basis (in regard to astronomic time or local time) for activation and deactivation. • Distinction between working days, weekend-days, holidays (fixed and variable), seperate days and summer/winter-days. • Minimal 16 entries to specify public street light behaviour. • Evening/morning lights to be operated identical as Night-lights in case this option is activated. For example of control-functionality refer to to Annex 2. | Yes/No
2.2.2.5 | MR | Control | Direct remote control of Public Street Lights (Evening/morning and Night) must be possible using JSON (refer Annex 7) and/or 104. Remote control must overrule locally stored Public light program. See Annex 2: Accompanying letter for details using 104 and/or JSON. | Yes/No
2.2.2.6 | AC | PLC | DALI box supports basic PLC functionality to compare measurements and I/O-status (e.g. to detect deviations in max. load or power consumption of Public Street Lights, when activated; Public Street Light load or powerconsumption available over P1 port input; refer 1.3.6). | Yes/No | Technical specification | 10 | Fixed (Yes: 10; No: 0)
2.2.3 | Tariff control
2.2.3.1 | MR | Control | DALI-box must support a locally stored Tariff program. Tariff program is using the local timezone. | Yes/No
2.2.3.2 | MR | Control | Locally stored Tariff program must be centrally configurable/managable using JSON as descibed in Annex 7 or in case of 104 protocol by using a uploadable configuration file. See Annex 2: Accompanying letter for details using 104 and/or JSON. | Yes/No
2.2.3.3 | MR | Control | Tariff program must support: • Fixed time basis for activation and de-activation Tariff Output • Distinction between working days, weekend-days and holidays (fixed and variable) and seperate days. • Minimal 16 entries to specify Tariff switch behaviour. | Yes/No
2.2.3.4 | MR | Control | Direct remote control of Tariff must be possible. Remote control must overrule locally stored Tariff program. | Yes/No
2.2.3.5 | MR | Control | Only in case of support of P1 Smart Meter port (ref. 1.3.5): DALI-box should be able to transfer (copy) the Tariff status on the P1-port directly to its Tariff Output (DO 3). Commanding DO 3 based on locally stored Tariff program or Tarfiff status Smart Meter input (P1-port) should be remotely configurable. | Yes/No
2.3 | Data processing
2.3.1 | General
2.3.1.1 | MR | Events and alarms | Events (including status of all DI's) and alarms must be transmitted, processed and implemented immediately using JSON as described in Annex 7 and/or 104. See annex 2: Accompanying letter for details using 104 and/or JSON. | Yes/No
2.3.1.2 | MR | Data availability | Data must not be compromised in case of power failure. Stored data must stay available after power failure. | Yes/No
2.3.2 | Load management and related purposes
2.3.2.1 | MR | Data processing | Below stated measurement-data (only transformer load) must be processed and transmitted by default on daily basis (meant for load management-purposes): Daily maximum (00:00-24:00 hours) of: • Voltage, 3 phase • Current, 3 phase • Total active power, S 3 phase • Total reactive power, S 3 phase • Total energy (counter), delivery and re-delivery (at 24:00 hours) • Only in case of support P1-port Smart Meter Public street Lights (refer 1.3.6): energy counters (at 24:00 hours). Daily minimum (00:00-24:00 hours): • Voltage, 3 phase • Total active power, S 3 phase • Total reactive power, S 3 phase Remote configuration options to select/deselect above mentioned variables must be available. | Yes/No
2.3.2.2 | MR | Data processing | Below stated measurement-data (for transformer load as wel as optional outgoing feeders) must be processed and transmitted immediately (meant for operational purposes): • Voltage, 3 phase, actual value • Current, 3 phase, actual value • Total active power, S 3 phase, actual value • Total reactive power, S 3 phase, actual value • Active power, 3 phase, actual value • Reactive power, 3 phase, actual value • THDi, 3 phase, actual value. • Only in case of support P1-port Smart Meter Public street Lights (refer 1.3.6): Total active power, S 3 Phase, actual value. Remote configuration options to select/deselect above mentioned variables must be available. Refresh of measurement-data must be based on offset value (threshold), with minimum and maximal constraints. Offset value: if an actual measurement value exceeds the previous measurement-value transmitted by more than the offset-value, an updated measurement-value must be transmitted. Enexis must be able to configure the offset value for each measurement as a percentage (default 5%, excluding voltage) and as a fixed value (voltage: 1 volt). Minimal and maximal constraints must be remotely configurable (e.g.: maximum number of transmissions: once every 1 second; minimum number of transmissions: once every 60 minutes). Remote rebooting of the system, in order to process an updated offset-value, is accepted. | Yes/No
2.3.2.3 | MR | Data processing | Below stated measurement-data (for transformer load as wel as optional outgoing feeders) must be proccessed on a, remotely configurable, fixed time basis (e.g. every 15 minutes or never) and must be stored locally on FIFO-basis. Local stored measurement-data must be retrievable over data files (for grid analysis purposes): • Voltage, 3 phase, average value • Current, 3 phase, average value • Active power, 3 phase, average value • Reactive power, 3 phase, average value • Total Harmonic Distortion in current (THDi), 3 phase, average value • Only in case of support P1-port Smart Meter Public street Lights (refer 1.3.6): Active power, 3 phase, average value. Local registration interval must be configurable remotely (default 5 minutes). The memory must be sufficient (and remain available) to store above mentioned measurement-data with timestamp on 1 minute basis for transformer load and on 5 minute basis for max. 12 optional outgoing feeders during at least one month. | Yes/No
2.3.2.4 | MR | Data processing | All measurement-data must be transmitted to central OT-domain in non-scaled format. | Yes/No
2.3.3 | Public Light control
2.3.3.1 | MR | Data processing | Status of DO's (Evening/morning and Night relays) must be transmitted to central OT domain upon change or on request from the central OT domain using JSON as described in Annex 7 and/or 104. See annex 2: accompanying letter for details using 104 and/or JSON. | Yes/No
2.3.4 | Tariff control
2.3.4.1 | MR | Data processing | Status of DO (Tariff relay) must be transmitted to central OT domain upon change or on request from the central OT domain using JSON as described in Annex 7 and/or 104. See annex 2: accompanuing letter for details using 104 and/or JSON. | Yes/No
2.4 | Logging/Management and Monitoring
2.4.1 | MR | Dataprocessing/ local syslog | Interruptions to the normal operation or relevant events (e.g. from modem/router, RTU, RTC) such as (local) communication failure, resetting IEC 60870-5-104 application, datastorage issues due to memory limitations etc. must be logged in a local syslog or syslogs including time label, to enable subsequent fault analysis. Logging must be available locally at least 7x24 hours. | Yes/No
2.4.2 | AC | Dataprocessing/ SNMP | Monitoring of relevant system-events and measurements on the health of the system, its componenents and the communication is possible using SNMPv3. Tenderer provides a relevant MIB for this purpose. | Yes/No | Technical specification | 10 | Fixed (Yes: 10; No: 0)
2.5 | Timekeeping
2.5.1 | MR | Timekeeping | The system must be provided with an NTP client in order to obtain the correct time of two (configurable) NTP servers. NTP version 6 is to be supported. The RTU must provide timestamps to events in UTC time. | Yes/No
2.5.2 | MR | Timekeeping | The system must provide a Real Time Clock (RTC). During power-outage the clock must keep functioning for at least 7x24 hours. The use of seperate replacable batteries for power back-up of the RTC is not allowed. When the system boots, the RTC time is initially used (until syncing with NTP is possible). The RTC is periodically synchronised by the NTP-time. When correct time during start-up is not guaranteed a default time/date must be loaded and this must be logged in the syslog. | Yes/No
2.5.3 | MR | Timekeeping | NTP is used for clock synchronization. Enexis will synchronize all box clocks via the (mobile) network using an NTP server (to be defined by Enexis if this is the controlling station, server or another system). The NTP time value is UTC. All events, logs and 104/JSON time tags are in UTC (2.2.1.1). For public lighting (2.2.2) and tariff switching (2.2.3) the local timezone is used as reference. The box must convert the UTC to local time with day light saving for this purpose. | Yes/No
3. | Operating conditions
3.1 | Environment
3.1.1 | MR | Environment | The cabinet including the installed components must be suitable for following ambient conditions: • temperature: -20 to +55 degrees Celsius • humidity: 10-95% non-condensing. | Yes/No
3.1.2 | MR | Environment | The following immunity requirements apply to the assembly of components (or its inputs and outputs where relevant): • Electrostatic discharge: IEC 61000-4-2 class 3, 8kV/Air and 6kV/Contact | Yes/No
3.1.3 | MR | Environment | The following immunity requirements apply to the assembly of components (or its inputs and outputs where relevant): • EMC: IEC 61000-4-3 class 3, 10V/m | Yes/No
3.1.4 | MR | Environment | The following immunity requirements apply to the assembly of components (or its inputs and outputs where relevant): • Fast Transient Burst (5nS/50nS): IEC 61000-4-4, 2kV | Yes/No
3.1.5 | MR | Environment | The following immunity requirements apply to the assembly of components (or its inputs and outputs where relevant): • Surge protection (1,2/50µS): IEC 61000-4-5 class 3, 2kV CM and 1kV DM | Yes/No
3.1.6 | MR | Environment | The following immunity requirements apply to the assembly of components (or its inputs and outputs where relevant): • Conducted Radio Frequency: IEC 61000-4-6 class 3, 10V | Yes/No
3.1.7 | MR | Environment | The following immunity requirements apply to the assembly of components (or its inputs and outputs where relevant): • Magnetic fields 50Hz: IEC 61000-4-8, level 3, 10A/m permanent and 100A/m 1-3 sec. | Yes/No
3.1.8 | MR | Environment | The following immunity requirements apply to the assembly of components (or its inputs and outputs where relevant): • Damped oscillating waves (1MHz burst): IEC 61000-4-18, 1kV DM/2,5kV CM | Yes/No
3.1.9 | MR | Environment | The assembly of components shall comply with acceptance criteria class 2 of chapter 7.5 of IEC 61850-3 and table 23 of IEC 60255-26. | Yes/No
3.2 | Lifetime, failure rate and proven technology
3.2.1 | MR | Lifetime | Technical lifetime must be minimum 10 years, with cumulatively failure-rate of max. 15%, based on the following environmental conditions: • temperature: -20°C (1% time), +20°C (98% time), +55°C (1% time) • humidity: 40% (5% time), 65% (85% time), 95% (10% time). | Specify lifetime
3.2.2 | AC | Annual failure rate | Specify cumulatively and annual failure-rate over 10 Years of service, based on conditions as specified in 3.2.1. | Specify cumulatively and annual failure rate/year over 10 years of service. In case of no specifications, a cumulatively failure rate of 15% over 10 years of service will be used as default. | TCO |  | Refer Price-sheet
3.2.3 | AC | Annual failure rate over lifetime period | Tenderer can prove its failure-rate of assembly or major parts, e.g. over MTBF-calculations, failure-analysis or similar. Please provide evidence. | Provide evidence by means of: 1) theoretical analysis based on FMEA and risk analysis by means of reliability statistics (= MTBF calculation) 2) Failure rate expectation over lifetime by means of accelarated life cycle testing on test samples | Technical specification | 15 | Fixed (0=No evidence; 5=MTBF calculation RTU+Modem; 10=MTBF calculation assembly; 15=Failure analysis assembly by testing)
3.2.4 | AC | Proven Technology | Switching functionality over pre-defined switchingprograms based on astronomic criteria (e.g. for Public Street Lights), is proven technology for the product(-line) offered. Proven technology means that the offered product(-line) is in use by one or more customers for at least 6 months. The contracting authority would like to receive evidence of the technology being a proven technology as stated above. | Yes/No; please provide evidence. | User-friendliness | 20 | Fixed (0=No; 20=Yes)
3.3 | Maintenance
3.3.1 | AC | Maintenance | Enexis intends not to perform any preventive inspection and maintenance activities (only reactive maintenance based on alarms). If correct operation of the system incorporates maintenance (e.g. changing batteries and/or electrolytic capacitors during by Enexis stated minimum lifetime), this must be specified by the Tenderer. | Specify maintenance requirements if applicable | User-friendliness | 10 | Fixed (Maintenance required=0, No maintenance required=10)
4. | Software/tools/systems
4.1 | General Software requirements
4.1.1 | MR | General software requirement | The software used must be fully compliant with following TCP/IP RFCs: • TCP/IP: RFC 1122 (https://tools.ietf.org/html/rfc1122). • IPv6: RFC 6540 (https://tools.ietf.org/html/rfc6540). | Yes/No
4.1.2 | MR | General software requirement | Software must be IPv6 compatible as well as IPv4 compatible. It must be possible to switch over from IPv4 to IPv6 remotely in the future. | Yes/No
4.2 | Configuration and commissioning tools
4.2.1 | MR | Configuration management | Tenderer is responsible for delivery of pre-configured (basic settings to facilitate comissioning process) DALI-boxes including installed SIM-cards (provided by Enexis), which are not yet assigned to a specific location or secondary substation. Substation-specific configuration settings will be added during commissioning-process. | Yes/No
4.2.2 | MR | Configuration management | Tenderer must provide a commissioning tool to remotely commission and configure DALI-boxes when first connected. Commissioning-tool must facilitate data-import functionality (CSV, XML or JSON format to be defined by supplier and handed over to Enexis) for substation-specific configuration settings. An alternative solution is that tenderer develops an import function in the commissioning tool for the file mentioned above. Hardware (server) to run this management-tool must be included in the offer. Refer Annex 2: accompanying letter. | Yes/No
4.2.3 | MR | Configuration management | Tenderer must provide a management tool to remotely manage DALI-boxes (firmware updates, patches and/or configuration changes). Management-tool must facilitate data-import functionality. Hardware (server) to run this management-tool must be included in the offer. Refer Annex 2: accompanying letter. | Yes/No
4.2.4 | AC | Configuration management | Tenderer provides a userfriendly, preferably automated, authentication process of DALI-boxes. Result is an operational communication-interface between central OT-domain and DALI-box (ready to transfer substation-specific configuration data). Manual configuration activities performed locally over web interface or configuration-tools are not accepted. Refer to Enexis commissioning process in Annex 2: Accompanying letter. | Please specify in detail each action needed to achieve an accepted, operational communication path between central OT-system and DALI-box. | User-friendliness | 30 | Fixed (30=outstanding functionality: no manual interventions during commissioning are needed; each manual intervention -5 points, minimum = 0 points).
4.2.5 | AC | Configuration management | Tenderer provides a userfriendly, preferably automated, configuration process, taking into account substation specific configuration parameters (e.g. security-credentials, transformer ratio current sensors; which MV-bays are remotely monitored over short circuit indicators). Manual configuration activities performed locally over web interface or configuration-tools are not accepted. Refer to Enexis commissioning process in Annex 2: Accompanying letter. | Please specify in detail each action needed to achieve an fully functional DALI-box, based on Enexis commissioning process. | User-friendliness | 30 | Fixed (20=outstanding functionality: no manual interventions during commissioning are needed; each manual intervention -5 points, minimum = 0 points).
4.2.6 | MR | Memory storage | Apart from having sufficient memory to store readings as specified elsewhere in this specification, the memory space must be sufficient to store at least two firmware and configuration versions. It must be possible to store one actual and one backup/new version, in order to remotely update de DALI-box | Yes/No
4.2.7 | MR | Impactfull commands | Impactful commands (switch-command, software changes, reset, etc.) must be protected for accidental change. | Yes/No
5. | Documentation, training, service and support
5.1 | Documentation
5.1.1 | MR | Instruction manual | Selected participant must provide two product manuals in Dutch: • an expert-manual for system engineers of the (remote) OT-management department. At least must be covered: specification of software/hardware configuration, remote configuration-tools, local web-interface, expert troubleshoot options (focus software) and remote management of DALI-boxes. • a quick start guide for field staff responsible for mounting and commissioning DALI-boxes. At least must be covered: system-overview of main components and slots, connection-diagrams, commissioning-procedures, basic troubleshoot options (focus hardware), Last gasp replacement procedures (if applicable) and explanation of local status-visualisation. | Yes/No
5.2 | Schemes
5.2.1 | MR | Schemes | All drawings must be provided digitally in a vector (DXF) format after awarding. | Yes/No
5.3 | Training
5.3.1 | AC | Training | Tenderer should facilitate an adequate system-engineer training (engineers OT-department) in Dutch or English (at minimum level B2 of the European framework of references, refer Annex 11, sub-annex 2). System-engineers must be able to set up and manage software templates, facilitate central commissioning, manage remote updates (firmware, configuration-files and settings), handle and interpret log files, carry out detailed fault diagnosis independently and manage centrally stored data. (Premise: two training courses in the Netherlands/total max. 10 system-engineers). | Specify training-duration, with a minimum of 2 days or more if found necessary based on complexity of solution (offer can be included in Reply format Price sheet). | User-friendliness | 5 | Fixed, linear (5 or more training days needed=0; 2 training days = 5; linear score in between)
5.3.2 | AC | Training | Tenderer should facilitate an adequate field staff training in Dutch (at minimum level B2 of the European framework of references, refer Annex 11 sub-annex 2). Core users must be able to understand the functionality of the used products/components in basic for Enexis Use-cases, commission systems and be able to perform a basic fault diagnosis (without tooling) independently. They should be able to train commissioning engineers independently. (Premise: 2 training-courses in the Netherlands /total approx. 16 core-users in total). In order to meet the Enexis practice, the Enexis specific parameters/configuration settings need to be included in these courses. | Specify training-duration, with a minimum 0f 0,5 days or more if found necessary based on complexity of solution (offer can be included in Reply format Price sheet). | User-friendliness | 5 | Fixed, linear (2 or more days needed = 0; 0,5 days = 5; linear score in between)
5.4 | Support and development
5.4.1 | MR | Support/SLA | Tenderer shall provide initial expert-support in Dutch or English (minimum level B2 according to the European framework of references), during normal working hours CE(S)T to facilitate correct initial installation of central software tools and correct functioning of the DALI-boxes. | Yes/No
5.4.2 | MR | Support/SLA | Tenderer shall provide software-engineering expertise during contract-period to implement additional requested functionality by Enexis. Support in Dutch or English (minimum level B2 according to the European framework of references) during normal working hours CE(S)T. | Yes/No; Specify development-expertise in €/hour all included in reply format Price sheet.
5.4.3 | MR | Support/SLA | Tenderer shall provide expert-support/assistance on distance in case of incidents or issues during contract-period in Dutch or English (minimum level B2 according to the European framework of references), during normal working hours CE(S)T. Below mentioned incident-levels are applicable: - Minor incident/issue: a hardware abnormality (≤ 4 DALI-boxes) or a disrupted support function is applicable, but business-critical parts of the application function properly and are not affected. Business-critical functions of the application are Public Streetlight Control, Tariff control and retrieving measurement data as well as short circuit indicator signals. - Major incident/issue: a hardware abnormality (5 ≥ x ≤ 14 DALI-boxes), a security-related issue or a (support) function indirectly affecting business-critical parts of the application is applicable. - Critical incident/issue: an incident/issue not classified as minor or major with business-critical impact. Below mentioned service-levels have to be met: - Minor incident/issue: will be under investigation within 5 working days and 90% of incidents/issues will be solved within 20 working days. - Major incident/issue: will be under investigation within 1 working day and 90% of incidents/issues will be solved within 10 working days. - Critical incident/issue: will be under investigation within 4 hours and 90% of incidents/issues will be solved by workaround within 8 hours. Final solution within 5 working days. In case of Major and Critical incidents a root cause analysis has been closed within two weeks after the incident. | Yes/No
5.4.4 | MR | Support/SLA | Tenderer will provide on-site support (during normal working hours CE(S)T) within 4 hours in case of critical incidents (e.g. critical Public Street Light issues) during contract-period in Dutch or English (minimum level B2 according to the European framework of references). Time based on Enexis offices located in Weert or Zwolle. | Yes/No
5.4.5 | MR | Support/SLA | Tenderer shall provide support for client software (current version = N, N-1 and N-2) in combination with an operating system for at least 8 years after the delivery of the unit. This support includes: • Incident-management support (refer 5.4.2). • Provide software updates / improvements if applicable. • Pro-active reporting about relevant Cyber Security vulnerabilities. • Pro-active provision of security patches for vulnerabilities. • Software-engineering activities requested by Enexis based on fixed hourly rates. Preliminary activities for software update service incorporate: • Ongoing monitoring of announcements by third party software, like OS (via web portals) concerning the availability of new patch levels and releases. • Assessment of changes (bug fixes, security patches) in order to decide whether immediate integration and installation in the client's operational system is necessary. Measures for prompt delivery when a potential system risk is perceived to exist, with estimation of whether a system risk is present to be done by vendor: • Test the compatibility of the third party software updates to be delivered with the reference system and the client's project-specific system. • Eliminate any incompatibilities between the new third party software release and the application software system by modification of the application software. • Compilation and delivery of the system changes (patches) with documentation and test instruction. | Yes/No
5.4.6 | MR | Support/SLA | Tenderer shall provide support for hardware for at least 8 years after the delivery of the unit. This support includes: • Perform hardware-repair of DALI-boxes out of warranty period (based on mutually agreed fixed prices up front). • Report performed hardware-repairs. • Logistical handling of DALI-boxes send for repair. • Maintaining knowledge of the Enexis DALI-box • Maintaining tracability of used components. • Notifying of EOL of used components minimum 1 year before actual EOL-date. • Yearly evaluation meeting | Yes/No
5.4.7 | MR | Development | Any software modification shall be justified by the Tenderer, documented and tested (incl. regression). Software changes must be submitted in advance by the Tenderer (using release notes) and implemented by means of releasemanagement. Software-releases should be backwards compatible. Enexis reserves the right to not accept software-modifications if need can not be demonstrated and/or correct operation can not be guaranteed. | Yes/No
5.4.8 | MR | Development | Any hardware modification shall be motivated by the Tenderer, documented and tested. Hardware changes must be submitted in advance by the Tenderer (using release notes). Enexis reserves the right to not accept hardware-modifications if need can not be demonstrated and/or correct operation can not be guaranteed. | Yes/No
Communication Requirements (Refer Annex 4)
2.1 | Cellular standard
GUL 1 | MR | Cellular standard | The communication unit shall support 2G (GPRS/EDGE), 3G (UMTS/HSPA), 4G (LTE) communication technology. | Yes/No
2.2 | Supported 3GPP release and device category
G 2 | MR | Supported 3GPP release and device category | The communication unit shall be GPRS/EDGE (EGPRS) capable type 1 MS having at least GPRS and EGPRS multislot class 10 capability. | Yes/No
U 2 | MR | Supported 3GPP release and device category | The communication unit shall be at least HSPA UE of HS-DSCH category 10, E-DCH category 5. | Yes/No
L 2 | MR | Supported 3GPP release and device category | The communication unit shall be category 1 LTE UE. | Yes/No
GUL 3 | MR | Supported 3GPP release and device category | The communication unit shall be 3GPP compliant UE. | Yes/No
GUL 4 | MR | Supported 3GPP release and device category | The communication unit shall be GCF certified. | Yes/No
L 5 | MR | Supported 3GPP release and device category | The communication unit shall support 20 MHz LTE system bandwidth on LTE. | Yes/No
2.3 | Supported frequency bands
GUL 6 | MR | Supported frequency bands | The communication unit must support GSM/UMTS/LTE frequencies used by the Dutch telecommunication providers. | Yes/No
2.4 | Signal reception & transmission characteristics
GUL 7 | MR | Signal reception & transmission characteristics | The communication unit shall have high receiver sensitivity on GSM, UMTS and LTE. | Yes/No
GUL 8 | MR | Signal reception & transmission characteristics | The communication unit must have sufficient output power in GSM, UMTS and LTE. | Yes/No
GUL 9 | MR | Signal reception & transmission characteristics | The communication unit shall support receive diversity for all bands in all supported technologies. | Yes/No
GUL 10 | MR | Signal reception & transmission characteristics | Communication unit shall be able to use optional external antenna in order to improve signal reception. | Yes/No
2.5 | Signal strength indications
GUL 11 | Optional (No MR/AC) | Signal strength indications | Process display of Dali box shall indicate general connectivity status towards the mobile network as well as other interfaces and sensors. | Yes/No
2.6 | Inter technology operation
GUL 12 | MR | Inter technology operation | Communication module shall successfully execute handovers and reselections between RAT’s. | Yes/No
2.7 | SIM card aspects
GUL 13 | MR | SIM card aspects | The communication unit supplier shall support 2FF UICC. | Yes/No
GUL 14 | MR | SIM card aspects | The communication unit shall support Gemalto’s MIM audit feature as well as multiple IMSI numbers on the SIM card and the automatic switching of IMSI numbers (by a SIM Tool Kit, STK application) and switching of IMSI numbers using 'Over The Air', OTA configuration. | Yes/No
2.8 | SMS
L 15 | MR | SMS | The communication unit in Dali box shall support SMS over LTE NAS signalling. | Yes/No
2.9 | IPv6 support
GUL 16 | MR | IPv6 support | The communication unit in Dali box shall support IPv4 and IPv6. | Yes/No
2.10 | Support for on-device timers
GUL 17 | MR | Support for on-device timers | The communication unit shall support ‘Minimum Periodic Search Timer’. | Yes/No
GUL 18 | MR | Support for on-device timers | The communication unit shall support T3245 timer functionality. | Yes/No
3.1 | Security aspects
GUL 19 | MR | Security aspects | The communication unit in Dali box shall ensure that parameters provided in the UICC (USIM) take precedence over parameters provided in the MTC device. | Yes/No
GUL 20 | MR | Security aspects | The communication unit in Dali box shall have unique IMEI resistant to tampering. | Yes/No
GUL 21 | MR | Security aspects | Dali RTU shall support UICC requirements defined by 3GPP. | Yes/No
3.2 | Device management and firmware updates
GUL 22 | MR | Device management and firmware updates | The communication module shall support secure updates of application software and firmware. | Yes/No
GUL 23 | MR | Device management and firmware updates | The communication module shall support remote firmware update functionality. | Yes/No
GUL 24 | MR | Device management and firmware updates | The communication module shall be able to resist unauthorized firmware update. | Yes/No
GUL 25 | MR | Device management and firmware updates | The communications module shall support standards based firmware update mechanisms. | Yes/No
3.3 | Application layer requirements
GUL 26 | MR | Application layer requirements | Communication unit shall be able to initiate communication towards SCADA server using open source and standardised secure protocols. | Yes/No
GUL 27 | MR | Application layer requirements | Dali box shall support the ‘last gasp’ functionality in case of power failure, by switching to battery backup supply in order to transmit critical events towards the central system. | Yes/No
GUL 28 | MR | Application layer requirements | SCADA central system shall be able to send prioritized switching commands to the Dali box i.e. to control public streetlights and these commands must be executed immediately. | Yes/No
GUL 29 | MR | Application layer requirements | The Dali box shall minimize the number of network connections by utilizing data aggregation and compression mechanisms. | Yes/No
GUL 30 | MR | Application layer requirements | The Dali box shall use dynamic polling interval for “always on” type of communication requiring ‘keep alive’ messages. Alternatively, it shall use fixed polling interval with optimized polling interval. | Yes/No
3.3 | Logging
GUL 31 | MR | Logging | Dali box shall support internal logging of relevant network parameters and overall service. | Yes/No
4.1 | Information exchange over cellular network
GUL 32 | MR | Information exchange over cellular network | Communication module shall support poll mechanism in communication with SCADA server. | Yes/No
GUL 33 | MR | Information exchange over cellular network | Communication module shall support connection establishment initiated by Enexis server in SCADA central system from both idle and connected mode. | Yes/No
GUL 34 | MR | Information exchange over cellular network | Dali box must be able to automatically recover from communication problems, using a randomising algorithm to re-establish the PDN connection. | Yes/No
GUL 35 | MR | Information exchange over cellular network | In case of network problems during an on-going communication session, the Dali box shall automatically return to the situation before the communication session, using a randomising reconnect algorithm. | Yes/No
4.2 | Requirements for device – network interaction
L 36 | MR | Requirements for device – network interaction | The communication unit shall support ‘low priority indicator’. | Yes/No
GUL 37 | MR | Requirements for device – network interaction | The communication unit shall support standardized connection efficiency features. | Yes/No
GUL 38 | MR | Requirements for device – network interaction | Watchdog mechanism shall be supported by the Dali box ensuring correct functionality and co-existence with other implemented mechanisms/features. | Yes/No
Security Requirements (refer Annex 5)
SFR | Future-Proof Design
SFR.01.1 | MR | Future-Proof Design | The DALI box SHALL have sufficient reserves in memory and computing power to allow updates to security functions that security experts anticipate are necessary during the DALI box’s lifecycle. | Yes/No
SPR | Cryptographic Algorithms and Key Lengths
SPR.01.1 | MR | Cryptographic Algorithms and Key Lengths | The DALI box SHALL use for security functions only cryptographic algorithms for which a description is publicly available, and which have been thoroughly reviewed by independent cryptographers. | Yes/No
SPR.01.2 | MR | Cryptographic Algorithms and Key Lengths | The DALI box SHALL not use for security functions a choice of cryptographic algorithms, protocols, and parameters if there are vulnerabilities known for it. | Yes/No
SPR.01.3 | MR | Cryptographic Algorithms and Key Lengths | If for a security function algorithms are available in [12], the DALI box SHALL use one of these algorithms. | Yes/No
SPR.01.4 | MR | Cryptographic Algorithms and Key Lengths | The DALI box SHALL use from [12] only those cryptographic algorithms, and parameters considered suitable for legacy or future use. | Yes/No
SPR.01.5 | MR | Cryptographic Algorithms and Key Lengths | The DALI box SHALL implement the algorithms in [12] exactly as they are described there without any modifications. | Yes/No
SPR.02.1 | MR | Cryptographic Random Number Generation | The DALI box SHALL use a dedicated cryptographic pseudo-random number generator, as defined in FIPS 186-2 [24], FIPS 140-2 (Annex C) [26], AIS 20 [26], or AIS 31 [27], to generate random numbers used for security functions. | Yes/No
SCR | Communication Security
SCR.01.1 | MR | Confidentiality | The DALI box SHALL protect the confidentiality of communication on the central systems interface by encrypting it using a protocol allowed by SPR.01. | Yes/No
SCR.02.1 | MR | Message Integrity and Authentication | The DALI box SHALL verify the integrity of application layer messages received on the central systems interface using a message authentication algorithm allowed by SPR.01. | Yes/No
SCR.02.2 | MR | Message Integrity and Authentication | If the DALI box detects that a message has been modified or if it cannot verify the integrity of the message, it SHALL reject or drop the message. | Yes/No
SCR.02.3 | MR | Message Integrity and Authentication | The DALI box SHALL allow parties it communicates with on the central systems interface to verify the integrity of application layer messages it sends by using a message authentication algorithm allowed by SPR.01. | Yes/No
SCR.02.4 | MR | Message Integrity and Authentication | The DALI box SHALL be able to determine that the sender of a message is a specific host in the DA system. | Yes/No
SCR.03.1 | MR | Message Freshness | The DALI box or modem SHALL be able to detect replay attacks on the central systems interface. | Yes/No
SCR.03.2 | MR | Message Freshness | If the DALI box detects that a message is replayed, it MUST reject or drop the message. | Yes/No
SCR.04.1 | MR | IPSec Interoperability | If the DALI box uses Ipsec for encryption and authentication on the central systems interface, it SHALL support the following IPsec settings: a. For encryption 256 bit ENCR_AES_CBC b. For authentication: SHA_256_128 HMAC c. For key establishment: Diffie-Helman with a 2048-bit MODP Group d. Support for both pre-shared keys (PSK), and certificates | Yes/No
SCR.04.2 | MR | IPSec Interoperability | If the DALI box uses Ipsec for encryption and authentication on the central systems interface, it SHALL apply filtering on the IP-traffic on the WAN interface. | Yes/No
SCR.04.3 | MR | IPSec Interoperability | If the DALI box uses Ipsec for encryption and authentication on the central systems interface, it SHALL be fully compliant with IKEv2 (RFC7296). | Yes/No
SCR.04.4 | MR | IPSec Interoperability | If the DALI box uses Ipsec for encryption and authentication on the central systems interface, it SHALL act as an IPsec initiator: it SHALL establish tunnel connections to the VPN servers automatically. | Yes/No
SCR.04.5 | MR | IPSec Interoperability | If the DALI box uses Ipsec for encryption and authentication on the central systems interface, it SHALL automatically re-establish closed or disconnected IPsec tunnels. | Yes/No
SCR.04.6 | MR | IPSec Interoperability | If the DALI box uses Ipsec for encryption and authentication on the central systems interface, it SHALL support assignment of virtual IP addresses through the IKEv2 configuration payload. | Yes/No
SCR.04.7 | AC | IPSec Interoperability | If the DALI box uses Ipsec for encryption and authentication on the central systems interface, it SHOULD support two parallel IPsec tunnels to allow it to connect to the two different control centers of Enexis. | Yes/No | Security | 15 | Fixed (two or more tunnels = 15 points; one tunnel = 0 pionts)
SSR | Software Security
SSR.01.1 | MR | Remote Software Updates | The DALI box SHALL support remote software updates. | Yes/No
SSR.01.2 | MR | Remote Software Updates | The DALI box SHALL support remotely updating all security functions. | Yes/No
SSR.01.3 | MR | Remote Software Updates | The DALI box SHALL support remotely updating the drivers of the RJ45 interface. | Yes/No
SSR.02.1 | AC | Software Integrity | The DALI box SHOULD verify the integrity of software before it is installed. | Yes/No; A description of the firmware update process and the security measures used in it, should be provided in the supporting documentation. | Security | 2 | Fixed (yes = 2 points; no = 0 points)
SSR.02.2 | AC | Software Integrity | The DALI box SHOULD reject software if it detects it has been modified, or it cannot verify the software’s integrity. | Yes/No; A description of the firmware update process and the security measures used in it, should be provided in the supporting documentation. | Security | 3 | Fixed (yes = 3 points; no = 0 points; points are only given if SSR.02.1 is also met)
SSR.03.1 | AC | Software Non-Repudiation | The DALI box SHOULD support non-repudiation for software: it SHOULD be able to prove that the software came from the Vendor. | Yes/No; A description of the firmware update process and the security measures used in it, should be provided in the supporting documentation. | Security | 5 | Fixed (yes = 5 points; no = 0 points; points are only given if SSR.02.1 and SSR.03.1 are also met)
SHR | System Hardening
SHR.01.1 | MR | Software Service Hardening | The DALI box SHALL have all unneeded services and applications removed, or disabled if removal is not possible. | Yes/No
SHR.01.2 | MR | Software Service Hardening | The DALI box SHALL not use services or applications for security functions if there are vulnerabilities known for them. | Yes/No
SHR.01.3 | MR | Software Service Hardening | The DALI box SHALL use only communication protocols that are needed to meet the functional requirements. | Yes/No
SHR.02.1 | MR | Account Hardening | The DALI box MUST NOT contain active default, guest and anonymous accounts. | Yes/No
SHR.02.2 | MR | Account Hardening | The DALI box MUST NOT allow remote access to root accounts on the DALI box. | Yes/No
SHR.02.3 | MR | Account Hardening | The DALI box SHALL have Vendor-owned accounts removed where feasible. | Yes/No
SRR | Resilience
SRR.01.1 | MR | Input Validation | The DALI box SHALL verify that all input it receives is valid. | Yes/No
SRR.01.2 | MR | Input Validation | The DALI box SHALL reject or drop input that is invalid or for which the validity cannot be verified. | Yes/No
SRR.02.1 | MR | Fail-Secure Operation | The DALI box SHALL be fail-secure, i.e., it SHALL be designed to fail in a manner that limits any security compromise of its own operation and security compromise of other devices. | Yes/No
SRR.02.2 | MR | Fail-Secure Operation | The DALI box SHALL not leak confidential information, such as keys or credentials, during a failure. | Yes/No
SRR.02.3 | MR | Fail-Secure Operation | The DALI box SHALL protect the integrity of security critical data during failures. | Yes/No
SRR.02.4 | MR | Fail-Secure Operation | The DALI box SHALL not allow access controls to be bypassed remotely during failures. | Yes/No
SRR.02.5 | MR | Fail-Secure Operation | The DALI box SHALL restore availability after software failures as soon as possible. | Yes/No
SAR | Access Control and User Authentication
SAR.01.1 | MR | Basic Access Control | The DALI box SHALL restrict access to the configuration and firmware update functionality by using passwords or cryptographic keys. | Yes/No
SKR | Key and Credential Management
SKR.01.1 | MR | Key and Credential Updates | The DALI box MUST support remote updates of all credentials and cryptographic keys. | Yes/No
SKR.02.1 | MR | Password Storage | The DALI box SHALL store passwords salted and hashed using a cryptographic hash function allowed by SPR.01. | Yes/No
SLR | Logging
SLR.01.1 | MR | Logging Security Events | The DALI box SHALL log security events in a locally stored log. | Yes/No
SLR.01.2 | MR | Logging Security Events | The DALI box SHALL take measures to prevent that attackers can modify, delete or overwrite the security log to hide their traces. | Yes/No
SMR | Automated Configuration and Firmware Management
SMR.01.1 | MR | Batch Software Updates | The DALI box SHALL allow batch software updates. | Yes/No
SMR.01.2 | MR | Batch Software Updates | The Vendor SHALL supply the tools needed to perform batch software updates. The tools SHALL support upgrading groups of DALI boxes without further interaction. | Yes/No
SMR.01.1 | MR | Batch Configuration Changes | The DALI box SHALL allow batch configuration changes after the initial installation. | Yes/No
SMR.01.2 | MR | Batch Configuration Changes | The Vendor SHALL supply tools for batch configuration changes. | Yes/No
SMR.01.3 | MR | Batch Configuration Changes | The batch configuration tools SHALL allow at least the following parameters to be changed based on data from a simple text file (csv or xml): a. The station name b. The transfer ratio of the transformers c. The placement of the short-circuit indicators d. The IPsec address e. The IPsec keys | Yes/No
SDR | Product Lifecycle and Governance
SDR.01.1 | MR | Information Security Management System | The Vendor SHALL implement an information security management system (ISMS) the scope of which includes at least all systems used to develop, test, manufacture and provision the DALI boxes and any software and hardware tools needed for the maintenance of the DALI box. | Yes/No
SDR.01.2 | AC | Information Security Management System | The Vendor SHOULD have regular audits of the ISMS performed by an accredited external auditor. | Yes/No; Information on the auditor should be provided in the supporting documentation. | Security | 10 | Fixed (yes = 10 points; no = 0 points)
SDR.01.3 | AC | Information Security Management System | The Vendors SHOULD provide a proof of the audit to the Purchaser on request. | Yes/No | Security | 2 | Fixed (yes = 2 points; no = 0 points)
SDR.01.4 | AC | Information Security Management System | The Vendor SHOULD obtain an ISO 27001 certification for the ISMS. | Yes/No | Security | 2 | Fixed (yes = 2 points; no = 0 points)
SDR.01.5 | AC | Information Security Management System | The Vendor SHOULD make a proof of the certificate available on request. | Yes/No | Security | 2 | Fixed (yes = 2 points; no = 0 points)
SDR.01.6 | AC | Information Security Management System | The Vendors SHOULD share their security policies with the Purchaser. | Yes/No | Security | 2 | Fixed (yes = 2 points; no = 0 points)
SDR.02.1 | MR | Configuration Management System | The Vendor SHALL employ a configuration management system for the administration of (changes of) hardware configurations and source code of devices. | Yes/No
SDR.02.2 | MR | Configuration Management System | The Vendor SHALL ensure that the configuration management system stores for each change an explanation, the author, the parts changed, and the time at which it was made. | Yes/No
SDR.02.3 | AC | Configuration Management System | The Vendor SHOULD allow the purchaser to audit the configuration management system. | Yes/No | Security | 2 | Fixed (yes = 2 points; no = 0 points)
SDR.03.1 | MR | Secured Versioning | The Vendor SHALL ensure that all released versions of hardware and firmware of the DALI box are uniquely identifiable. | Yes/No
SDR.03.2 | MR | Secured Versioning | The Vendor SHALL provide to the Purchaser a cryptographic hash value for each firmware version. | Yes/No
SDR.03.3 | MR | Secured Versioning | The Vendor SHALL be able to reproduce released versions within the contractually agreed product lifecycle, with traceability provided by the hash value(s) as identifier(s). | Yes/No
SDR.03.4 | AC | Secured Versioning | The Vendor SHOULD digitally sign each firmware update supplied to the Purchaser. | Yes/No; Information on the firmware signing process should be provided in the supporting documentation. | Security | 5 | Fixed (yes = 5 points; no = 0 points)
SDR.03.5 | AC | Secured Versioning | The Vendor SHOULD protect the firmware signing keys as highly confidential data. | Yes/No; Security measures taken to protect the key should be briefly described in the supporting documentation | Security | 5 | Fixed (yes = 5 points; no = 0 points)
SDR.03.6 | AC | Secured Versioning | The Vendor SHOULD report it to the Purchaser if a firmware signing key is compromised. | Yes/No | Security | 5 | Fixed (yes = 5 points; no = 0 points)
SDR.04.1 | MR | Vulnerability Handling Process | The Vendor SHALL have an established and documented process to handle vulnerabilities. | Yes/No
SDR.04.2 | MR | Vulnerability Handling Process | The Vendor SHALL monitor information sources on vulnerabilities to determine if it has been affected. | Yes/No
SDR.04.3 | MR | Vulnerability Handling Process | The Vendor SHALL address vulnerabilities found by the Vendor itself, the Purchaser or system integrator, or external security researchers. | Yes/No
SDR.04.4 | MR | Vulnerability Handling Process | The Vendor SHALL disclose to the Purchaser all known vulnerabilities on the DALI box as soon as possible. | Yes/No
SDR.04.5 | MR | Vulnerability Handling Process | The Vendor SHALL communicate vulnerabilities to the Purchaser in a secure manner. | Yes/No
SDR.04.6 | MR | Vulnerability Handling Process | The Vendor SHALL issue a recommendation on how to mitigate a vulnerability as soon as possible. | Yes/No
SDR.04.7 | MR | Vulnerability Handling Process | The Vendor SHALL prioritize fixing vulnerabilities based on the potential impact to the Purchaser. | Yes/No
SDR.05.1 | MR | Security Updates and Patching | The Vendor SHALL provide security updates or patches for the DALI box to fix high impact vulnerabilities found during the DALI box’s lifecycle. | Yes/No
SDR.05.2 | MR | Security Updates and Patching | The Vendor SHALL test all security updates and patches prior to deployment. | Yes/No
SDR.05.3 | AC | Security Updates and Patching | The Vendor SHOULD provide documentation that all security patches were tested and validated prior to deployment. | Yes/No | Security | 5 | Fixed (yes = 5 points; no = 0 points)
SDR.05.4 | AC | Security Updates and Patching | The Vendor SHOULD release a patch or firmware update for a vulnerability no more than three months after it was reported to the Vendor. | Yes/No | Security | 5 | Fixed (yes = 5 points; no = 0 points)
SDR.06.1 | MR | Security Training and Awareness | The Vendor SHALL provide security training for the personnel. | Yes/No
SDR.06.2 | MR | Security Training and Awareness | The Vendor SHALL be able to document that the necessary knowledge to securely develop and securely produce products is in place. | Yes/No
SDR.06.3 | MR | Security Training and Awareness | The Vendor SHALL name a technical expert responsible for security-related matters who acts as contact person for the Purchaser. | Yes/No
SDR.06.4 | MR | Security Training and Awareness | The Vendor SHALL conduct a risk analysis of the firmware design and the corresponding system architecture. | Yes/No
SDR.06.5 | AC | Security Training and Awareness | The Vendor SHOULD provide documented professional experience in the area of IT security or a security certification, e.g., CISSP or CISM. | Yes/No; Certificates of relevant personnel should be included in the supporting documentation. | Security | 5 | Fixed (yes = 5 points; no = 0 points)
SUR | Assurance
SUR.01.1 | MR | Security Documentation | The Vendor SHALL provide documentation that describes in a traceable manner how each security requirements in this document has been implemented. | Yes/No
SUR.01.2 | MR | Security Documentation | The Vendor SHALL document which cryptographic algorithms, protocols, and parameters are used for which security functions. | Yes/No
SUR.01.3 | MR | Security Documentation | The Vendor SHALL document which cryptographic random number generator is used. | Yes/No
SUR.01.4 | MR | Security Documentation | The Vendor SHALL provide a step-by-step description of the firmware update process. | Yes/No
SUR.01.5 | MR | Security Documentation | The Vendor SHALL document all interfaces of the DALI box, including the protocols and services used on each interface. | Yes/No
SUR.01.6 | MR | Security Documentation | If interfaces or services are disabled and not removed, the Vendor SHALL provide information on how they have been disabled. | Yes/No
SUR.01.7 | MR | Security Documentation | The Vendor SHALL provide a list of all accounts enabled on the DALI box on delivery. | Yes/No
SUR.01.8 | MR | Security Documentation | The Vendor SHALL provide a list of all security events logged by the DALI box. | Yes/No
SUR.01.9 | MR | Security Documentation | The Vendor SHALL provide the above documentation together with its proposal. | Yes/No
SUR.01.10 | MR | Security Documentation | The Vendor SHALL allow verification of the design evidence by an independent third party selected by the Purchaser. | Yes/No
SUR.02.1 | MR | Security Testing | The Vendor SHALL perform tests to verify that all the security requirements in this document have been implemented correctly. | Yes/No
SUR.02.2 | MR | Security Testing | The Vendor SHALL test the complete functional scope of the DALI box, including the communication chain between the DALI box and all connected field devices and the central systems. | Yes/No
SUR.02.3 | MR | Security Testing | The Vendor SHALL clearly document the security tests. | Yes/No
SUR.02.4 | MR | Security Testing | The Vendor SHALL test each firmware release to ensure that it does not contain known vulnerabilities. | Yes/No
SUR.02.5 | MR | Security Testing | The Vendor SHALL allow the Purchaser to contract an independent test lab to perform a penetration test on the DALI box. | Yes/No
SUR.02.6 | AC | Security Testing | The Vendor SHOULD conduct robustness tests, such as fuzzing or flooding, on all protocols used by the device both on the application layer and on lower protocol layers. | Yes/No; The tests performed (including which protocols are tested) should be briefly described in the supporting documentation. | Security | 5 | Fixed (yes = 5 points; no = 0 points)
SUR.02.7 | AC | Security Testing | The Vendor SHOULD conduct design and code reviews and provide the results to the Purchaser. | Yes/No; The review process should be briefly described in the supporting documentation. | Security | 5 | Fixed (yes = 5 points; no = 0 points)
SUR.03.1 | AC | Secure Coding Practices | The Vendor SHOULD establish and enforce secure coding practices for the development of the DALI box following best practices. | Yes/No; The coding practicies should be briefly described in the supporting documentation. | Security | 5 | Fixed (yes = 5 points; no = 0 points)
SUR.03.2 | AC | Secure Coding Practices | The Vendor SHOULD establish an internal code review process that takes security into account. | Yes/No; The code review process should be briefly described in the supporting documentation. | Security | 5 | Fixed (yes = 5 points; no = 0 points)
SUR.03.3 | AC | Secure Coding Practices | The Vendor SHOULD use automated code analysis tools to find security vulnerabilities. | Yes/No; The tools used should be described in the supporting documentation. | Security | 5 | Fixed (yes = 5 points; no = 0 points)

## ItT - Reply format Commercial
Invitation to Tender DALI - Reply format Commercial
Please fill out the blue cells
Tenderer Name:
Reference to ItT-document | Requirement type AC=Awarding Criterium MR=Minimum req. | Requirement | Reply-format | Valuation category (if AC) | Max. score | Assessment method | Reply
[7 empty] | Yes/No | Specification
3. | Procedure Process & Conditions
3.11 | Consent conditions
3.11 | MR | unconditionally accepts conditions and requirements of this Invitation to Tender | Yes/No
3.11.1 | MR | Lawfully signed all the submitted documents | Yes/No
3.12 | Warranty
3.12 | MR | Warranty | Yes/No
4. | Grounds for Exclusion and Minimum Requirements for the Candidate
4.1 to 4.6 | MR | Grounds for Exclusion andRequirements for the Candidate | Yes/No
7. | Logistics
7.1 | Logistics condition
7.1 | MR | Logistics Condition | Yes/No
7.2 | Packing Requirements
7.2 | MR | Packing Requirements | Yes/No
7.3 | Stocking Requirements
7.3 | MR | Stocking Requirements | Yes/No; please list hazardous substances of battery and volume per battery
7.4 | Delivery times
7.4 | MR | Delivery times | Yes/No
7.5 | Return procedure
7.5 | MR | Return procedure | Yes/No
8. | Contract
8.2 | Drawing up of contract
8.2 | MR | Contract | Yes/No
8.2.1 | MR | Drawing up of contract | Yes/No